## SUMMARY
SUMMARY OF METERS
COMPLETION PER TEAM MEMBER
TJ | 26
OMAR | 4
PATRICK | 123
MICHAEL | 101
ANDREA | 97
MARCELA | 94
EMPTY | 0
METERS BY UTILITY TYPE
ELEC | 212
CHW | 120
STEAM | 105
TOTAL | 437
METERS BY METHOD
CALCULATED | 165
VIRTUAL | 41
BTU | 19
DEM | 160
PULSE | 14
SQUARE D | 7
STD FLOW | 0
MASS FLOW | 28
SUMMARY OF DAY32 POINTS
TOTAL # OF METER IDs * | 437
ELECTRICAL
TOTAL # OF ELECTRIC METER IDs | 213
# OF METER IDs THAT REQUIRE ALIAS(ES) | 177
# OF METER IDs ALREADY ALIASED | 178
% COMPLETION OF ALIAS IMPLEMENTATION | 100.6%
STEAM
TOTAL # OF STEAM METER IDs | 105
# OF METER IDs THAT REQUIRE ALIAS(ES) | 85
# OF METER IDs ALREADY ALIASED | 84
% COMPLETION OF ALIAS IMPLEMENTATION | 98.82%
CHILLED WATER
TOTAL # OF CHILLED WATER METER IDs | 119
# OF METER IDs THAT REQUIRE ALIAS(ES) | 98
# OF METER IDs ALREADY ALIASED | 93
% COMPLETION OF ALIAS IMPLEMENTATION | 94.9%
TOTAL # OF METER IDs REQUIRING ALIASES | 360
% COMPLETION OF OVERALL ALIAS IMPLEMENTATION | 98.61%
* These are the individual customers/utilities bill per type of utility (sum of elec, chw, steam individual bills for all campus customers)
** Note that the actual number of aliases in Desigo may be higher than the number of "meter IDs" already aliased.
This is because the consumption value of some meters depend on multiple BAS Points.
We have implementeed one alias per BAS point required to calculate the consumption value for a specific meter.
Alias implementation only encompasses BAS points containing current month readings (DAY 32).
test

## METERs
UTILITIES BILLING
METERS
TEAM MEMBER | METERID | TYPE | METHOD | MSTP/FLN/IP DEVICES | PHYSICAL POINTS | NOTES
MICHAEL | 105401EL | ELEC | DEM | DEG_E_DEM |  | BLDG 4023 NOT ON METERING SPREAD SHEET FOR ELEC. This device is just for monitoring not billing.
MICHAEL | 483233EL | ELEC | DEM | DEG_W_DEM |  | BLDG 4024 NOT ON METERING SPREAD SHEET FOR ELEC. This device is just for monitoring not billing.
MARCELA | CW0000 | CHW | CALCULATED | SP1_CH1, SP1_CH2, SP1_CH3, SP1_CH4, SP1_CH5, SP1_CH6 | [SP1_CH1CFM, SP1ST, SP1RT], [SP2RT, SP2ST, SP1_CH2CFM], [SP3RT, SP3ST, SP1_CH3CFM], [SP4ER, SP4ES, SP1_CH4CFM], [SP5ER, SP5ES, SP1_CH5CFM], [SP6ER, SP6ES, SP1_CH6CFM], [SP1_CHWR, SP1_CHWS, SP1_RET_FLOW] | NOT FINISHED NEED TO DO SAT2 AND CUP
ANDREA | CW0001 | CHW | CALCULATED | WC_CLG | RD_CWR, RD_CWS | METER NEEDS TO BE REPROGRAMED FOR TON OUTPUT NOT BTU'S
ANDREA | CW0002 | CHW | CALCULATED |  | DICWF, DICWR, DICWS
ANDREA | CW0002A | CHW | CALCULATED |  | DIUC02_CWR, DICWS, DIUC02_CWGPM
TJ | CW0003 | CHW | CALCULATED | DICWS | WICHRT, WICHST, WICHFL
TJ | CW0004 | CHW | CALCULATED |  | DHCWRT DHCWST DHCWF
TJ | CW0005 | CHW | CALCULATED |  | EPS_CHWSRT EPS_CHWSST EPS_CHWRF
OMAR | CW0006 | CHW | CALCULATED |  | PRCWF, PRCWR, PRCWS
ANDREA | CW0007 | CHW | CALCULATED |  | FA_SCPHR, FA_CWL, FA_CWF
ANDREA | CW0008 | CHW | CALCULATED |  | BECWRT, BECWST, BECWFL
ANDREA | CW0009 | CHW | CALCULATED |  | 0009_CHW_BLDG_FLOW, 0009_CHWRT, 0009_CHWST
ANDREA | CW0011 | CHW | CALCULATED |  | SHHR, SHAW_CWS, SHSCHF
ANDREA | CW0011A | CHW | VIRTUAL |  | SHAW_OLD_CWT | NO PHYSICAL POINT EXISTS :(
ANDREA | CW0012 | CHW | BTU | 0012-CHW-BTU |  | METER NEEDS TO BE REPROGRAMED FOR TON OUTPUT NOT BTU'S
ANDREA | CW0013 | CHW | CALCULATED |  | 0013_BLDGCHWR, 0013_BLDGCHWS, 0013_BLDGCHWFL
MICHAEL | CW0014 | CHW | DEM | 0014-CHW-ENERGY |  | ON THE BACNET PANEL
ANDREA | CW0015 | CHW | CALCULATED |  | BRCHRT, BRCHST, BRCHFL
ANDREA | CW0016 | CHW | CALCULATED |  | GHCHRT, GHCHSB, GHCHFL
ANDREA | CW0017A | CHW | CALCULATED |  | JO_AB3CWT, JO_CWS, JO_AB3CWF
ANDREA | CW0017B | CHW | VIRTUAL |  |  | CALCULATED USING CW0017A & CW0017C
ANDREA | CW0017C | CHW | CALCULATED |  | JO_CWF, JO_CWS, JO_BCWR
ANDREA | CW0017D | CHW | CALCULATED |  | JB_CHW_RT, JB_CHW_ST, JB_CHW_FLOW
ANDREA | CW0019 | CHW | CALCULATED |  | LS_CWS, LS_CWR, LS_CWF
ANDREA | CW0020 | CHW | CALCULATED |  | LPCWRT, LPCWST, SCCWF
ANDREA | CW0023 | CHW | CALCULATED |  | ROV_A_CWR, ROV_A_CWS, ROV_A_CWF
MICHAEL | CW0025 | CHW | CALCULATED |  | MGCWF, MGCWR, MGCWS
MICHAEL | CW0026 | CHW | CALCULATED |  | NACWF NACWS, NACWR
MICHAEL | CW0028 | CHW | CALCULATED |  | HCCWFL, HCCWRT, HCCWST
MARCELA | CW0030 | CHW | CALCULATED |  | MRT, MST, CUP_CWF
MICHAEL | CW0035 | CHW | CALCULATED |  | HOCWF, HOCWR, HOCWL
MICHAEL | CW0035A | CHW | VIRTUAL |  | HOCWF, HOCWR, HOCWL, 0036_OSB_CHW_BTU, 0037_CWF, 0037.FL.AHU13-14.FLCWR, 0037.FL.AHU13-14.FLCWS
MICHAEL | CW0036 | CHW | BTU | 0036_OSB_CHW_BTU
MICHAEL | CW0037 | CHW | CALCULATED |  | 0037_CWF, 0037.FL.AHU13-14.FLCWR, 0037.FL.AHU13-14.FLCWS
MICHAEL | CW0038 | CHW | CALCULATED |  | DTCWF, DTCWS, DTCWR
MICHAEL | CW0039 | CHW | BTU | 0039-CHW-ENERGY
MICHAEL | CW0040 | CHW | BTU | 0040_CHWBTU
MICHAEL | CW0041 | CHW | CALCULATED |  | KECWR, KECWS, KECWF
MICHAEL | CW0042 | CHW | CALCULATED |  | NUCWF, NUCWR, NUCWS
MICHAEL | CW0044 | CHW | CALCULATED |  | ROG_CHWRFLW, ROG_CHWR, ROG_CHWS
MICHAEL | CW0045 | CHW | CALCULATED |  | RI_CWF, RI_CWR, RI_CWS
MICHAEL | CW0046 | CHW | CALCULATED |  | SH_CWF, SH_CWR, SH_CWS
MICHAEL | CW0050 | CHW | CALCULATED |  | STN_CWF, STN_CWR, STN_CWS
MICHAEL | CW0052 | CHW | CALCULATED |  | ROV_B_CWF, ROV_B_CWR, ROV_B_CWS
MICHAEL | CW0054 | CHW | CALCULATED |  | 0054_CHILLWATERFLOW, 0054_CHWRETTEMP, 0054_CHWSUPPLYTMP
MICHAEL | CW0055 | CHW | CALCULATED |  | ED_CWF, ED_CWR, ED_CWS
MICHAEL | CW0057 | CHW | CALCULATED |  | PBCWFL, PBCWRT, PBCWST
MICHAEL | CW0070 | CHW | CALCULATED |  | PGCWFL, PGCWRT, PGCWLT
MICHAEL | CW0070A | CHW | CALCULATED | N/A | N/A | CALCULATED MANUALLY BY NARIMAN
MICHAEL | CW0070B | CHW | CALCULATED | N/A | N/A
MICHAEL | CW0072 | CHW | CALCULATED |  | LOCWF, LOCWR, LOCWS
MICHAEL | CW0074 | CHW | CALCULATED |  | LANDIS_CWF, LANDIS_CWR, LANDIS_CWS
MICHAEL | CW0075 | CHW | CALCULATED |  | MH_CWF, MH_CWR, MH_CWS
MICHAEL | CW0076 | CHW | CALCULATED |  | PSCWF, PSCWR, PSCWS
MICHAEL | CW0077 | CHW | CALCULATED |  | MAUC02_MACWF, MAUC02_MACWR, MAUC02_MACWS
MICHAEL | CW0085 | CHW | CALCULATED |  | CAWCCWF, CAWCCWR, CAWCCWS
ANDREA | CW0089 | CHW | CALCULATED |  | MS_CWF MS_CWR MS_CWS
ANDREA | CW0113 | CHW | BTU | 0113-CA-CHW-BTU
ANDREA | CW0114 | CHW | CALCULATED |  | ENGLAB_CWF, ENGLAB_CWR | A SUPPLY TEMP POINT EXISTS (ENGLAB_CWS) BUT IT IS NOT BEING USED WHEN CALCULATING THE METER, ONLY A 42.
ANDREA | CW0116 | CHW | CALCULATED |  | LV_CWF1, LVCWS, LVCWR
ANDREA | CW0116A | CHW | CALCULATED |  | NW4CF, NWC4R, NWC4S
ANDREA | CW0116B | CHW | VIRTUAL |  |  | CALCULATED USING CW0016A
ANDREA | CW0116C | CHW | VIRTUAL |  |  | CALCULATED USING CW0016A
ANDREA | CW0121C | CHW | BTU | 0121-CHW-ENERGY
ANDREA | CW0132 | CHW | CALCULATED |  | TGCWR, TGCWS, TGCWF
ANDREA | CW0134 | CHW | CALCULATED |  | SN_CWR, SN_CWS, SN_CWF
ANDREA | CW0134A | CHW | CALCULATED |  | SS_CWRT, SS_CHST, SS_CWF1
ANDREA | CW0135 | CHW | CALCULATED |  | SACWRT, SACWST, SACWF_
MICHAEL | CW0146 | CHW | CALCULATED |  | IMCHSF, IMCHR, IMCHS
MARCELA | CW0195 | CHW | BTU | 0195_BTU_METER
MARCELA | CW0223 | CHW | CALCULATED |  | STP_CHWR, STP_CHW, STP_CWF
MARCELA | CW0223A | CHW | VIRTUAL |  |  | CALCULATED FROM 0223, 0224, 0224TWS, 0226.
MARCELA | CW0224 | CHW | CALCULATED | UCB_CHW_BTU_EAST, UCB_CHW_BTU_WEST | UCB_CHW_BLD_CHWR, UCB_CHW_BLD_CHWS, UCB_CHW_BLD_CHWF, | BTU METERS FOR WHOLE 0224 BUILDING. THIS BILL IS 46.24 % OF THE WEST METER - PHYSICAL POINTS
MARCELA | CW0224TWS | CHW | CALCULATED | UCB_CHW_BTU_EAST, UCB_CHW_BTU_WEST | UCB_CHW_BLD_CHWR, UCB_CHW_BLD_CHWS, UCB_CHW_BLD_CHWF | BTU METERS FOR WHOLE 0224 BUILDING. THIS BILL IS 53.76 % OF THE WEST METER - PHYSICAL POINTS
MARCELA | CW0226 | CHW | CALCULATED |  | NTP1RT, NTP1ST, NTP1FL
MICHAEL | CW0260 | CHW | CALCULATED |  | LICHFL, LICHRB, LICHSB
MICHAEL | CW0293 | CHW | IGNORE | N/A | N/A | CHW METER HAS TO BE MANUALLY READ FOR BUILDING
PATRICK | CW0379 | CHW | CALCULATED |  | SV_BCWRF, SV_CWS, SV_BCWR
PATRICK | CW0379A | CHW | CALCULATED |  | SV_A11CWR, SV_A11CWF
PATRICK | CW0379B | CHW | CALCULATED |  | SV_A21CWR, SV_A21CWF
PATRICK | CW0379C | CHW | CALCULATED |  | SV_A31CWR, SV_A31CWF
PATRICK | CW0379D | CHW | CALCULATED |  | SV_A13CWR, SV_A13CWF
PATRICK | CW0379E | CHW | CALCULATED |  | SV_BCWRF, SV_CWS, SV_BCWR, SV_A11CWR, SV_A11CWF, SV_A21CWR, SV_A21CWF, SV_A31CWR, SV_A31CWF, SV_A13CWR, SV_A13CWF
TJ | CW0488 | CHW | CALCULATED |  | WDINING_CWR WDINING_CWS WDINING_CWRF
TJ | CW0495 | CHW | CALCULATED |  | REABCWR REACWS REACWSF
TJ | CW0496 | CHW | CALCULATED |  | REBBCWR REBCWS REBCWSF
TJ | CW0497 | CHW | CALCULATED |  | RECBWR RECCWS RECCWSF
TJ | CW0498 | CHW | CALCULATED |  | REDBWR REDCWS REDCWSF
TJ | CW4001 | CHW | CALCULATED |  | MED_SCH_CWR MED_SCH_CWS MED_SCH_CWSF
TJ | CW4004 | CHW | CALCULATED |  | PSY_CWR PSY_CWS PSY_CWSF
TJ | CW4007 | CHW | CALCULATED |  | LIFE_BCWR LIFE_BCWS LIFE_CWSF
TJ | CW4008 | CHW | CALCULATED |  | CHEM_CWR CHEM_CWS CHEM_CWF
TJ | CW4009 | CHW | CALCULATED |  | CLASS_BCWR CLASS_CWS CLASS_CWF
MARCELA | CW4010 | CHW | BTU | 4010-CHW-ENERGY |  | ONICON
MICHAEL | CW4011 | CHW | VIRTUAL |  |  | VIRTUAL CALCULATION
MARCELA | CW4018 | CHW | BTU | 4018_CHW_BTU_METER |  | ONICON
MARCELA | CW4018A | CHW | VIRTUAL |  |  | GSF BASED
MARCELA | CW4018B | CHW | VIRTUAL |  |  | GSF BASED
MICHAEL | CW4020 | CHW | CALCULATED |  | WILD_S_CWF, WILD_S_BCWS, WILD_S_BCWR
MICHAEL | CW4021 | CHW | CALCULATED |  | WILD_N_CWF, WILD_N_BCWS, WILD_N_BCWR
MICHAEL | CW4022 | CHW | BTU | WILD_3_CHW-BTU
MICHAEL | CW4023 | CHW | CALCULATED |  | DEG_E_CWF, DEG_E_CWR, DEG_E_CWS
MICHAEL | CW4024 | CHW | CALCULATED |  | DEG_W_CWF, DEG_W_CWR, DEG_W_CWS
MARCELA | CW4029 | CHW | CALCULATED | JBA_CHWBTUM | JBA_CHWCAMST, JBA_CHWCAMRT | FAILED. JBA_CHWBTUM (BTU METER FOR FLOW MEASUREMENT)
MARCELA | CW4029A | CHW | VIRTUAL
MARCELA | CW4029B | CHW | VIRTUAL
MARCELA | CW4029C | CHW | VIRTUAL
MARCELA | CW4029D | CHW | VIRTUAL
MARCELA | CW4029E | CHW | VIRTUAL
PATRICK | CW4030 | CHW | BTU | WEL_CHWBTU
ANDREA | CW4030A | CHW | VIRTUAL |  |  | CALCULATED USING CW4030
ANDREA | CW4030B | CHW | VIRTUAL |  |  | CALCULATED USING CW4030
ANDREA | CW4030C | CHW | VIRTUAL |  |  | CALCULATED USING CW4030
ANDREA | CW4030D | CHW | VIRTUAL |  |  | CALCULATED USING CW4030
MICHAEL | CW4031 | CHW | CALCULATED |  | STSC_S_HPSF, STSC_SD | STSC_S_HPSF, POINT IS FAILED
MARCELA | CW4060 | CHW | BTU | 4060_4060CHWBTU |  | APP 1996
MARCELA | CW4061 | CHW | BTU | 4060_4061CHWBTU |  | APP 1996
MARCELA | CW4062 | CHW | BTU | 4062_CHWBLD3BTU |  | APP 1996
MARCELA | CW4062A | CHW | BTU | 4062_CHWFSBTU |  | APP 1996
MARCELA | CW4063 | CHW | BTU | 4062_CHWBLD4BTU |  | APP 1996
MICHAEL | CW4090 | CHW | CALCULATED |  | 4090_CHW_SFLOW, 4090_CHW_RT, 4090_CHW_ST
MARCELA | E0000 | ELEC | SQUARE D | MAIN2 |  | MASTER METER FOR CAMPUS
ANDREA | E0001 | ELEC | DEM | WE_DEM
ANDREA | E0001A | ELEC | DEM | RD_DEM
ANDREA | E0002 | ELEC | DEM | DIF_DEM
ANDREA | E0002A | ELEC | DEM | DI_NODEKW
ANDREA | E0002B | ELEC | VIRTUAL |  |  | CALCULATED USING E0002 & E0002A
PATRICK | E0003 | ELEC | DEM | WIDEM
ANDREA | E0003A | ELEC | DEM | WIATTDEM
ANDREA | E0003B | ELEC | VIRTUAL |  |  | CALCULATED USING E0003 & E0003A
ANDREA | E0004 | ELEC | DEM | DH_DEM
ANDREA | E0005 | ELEC | DEM | EP_DEM
ANDREA | E0006 | ELEC | DEM | PR_DEM
ANDREA | E0007 | ELEC | DEM | FA_DEM
ANDREA | E0008 | ELEC | DEM | BE_KW
ANDREA | E0008A | ELEC | DEM | BELL_CELLTOWER
ANDREA | E0008B | ELEC | VIRTUAL |  |  | CALCULATED USING E0008 & E0008A
ANDREA | E0009 | ELEC | DEM | 0009_DEM
ANDREA | E0010A | ELEC | DEM | CONF-DEM
ANDREA | E0011 | ELEC | DEM | SHAW_KW
ANDREA | E0011B | ELEC | PULSE |  | 0011_METERING_SHKWHA
ANDREA | E0011C | ELEC | VIRTUAL |  |  | CALCULATED USING E0011 & E0011B
ANDREA | E0012 | ELEC | DEM | 0012_MAIN_DEM
ANDREA | E0013 | ELEC | DEM | 0013_MAIN.DEM
ANDREA | E0014 | ELEC | DEM | 0014_DEM1
ANDREA | E0015 | ELEC | PULSE |  | BRKWH
ANDREA | E0016 | ELEC | PULSE |  | GHKWH
ANDREA | E0017C | ELEC | CALCULATED | JO_DEM1, JO_DEM2, JO_DEM3 |  | CALCULATED BY SUBSTRACTING JO_DEM1 AND A VIRTUAL POINJT COMPRISING OF JO_DEM2 & JO_DEM3
ANDREA | E0017D | ELEC | CALCULATED | JO_DEM2, JO_DEM3
ANDREA | E0017E | ELEC | IGNORE | N/A | N/A | NOT NEEDED
ANDREA | E0017F | ELEC | VIRTUAL |  |  | CALCULATED USING E0017C & E0017D
ANDREA | E0017G | ELEC | DEM | JB_DEM
PATRICK | E0019 | ELEC | DEM | LS_DEM |  | FAILED
ANDREA | E0020 | ELEC | CALCULATED | DIRAC_COMP, DIRAC_DEM
ANDREA | E0020A | ELEC | PULSE |  | SCKWHN
ANDREA | E0020B | ELEC | VIRTUAL |  |  | CALCULATED USING E0020, E0020A & E0020C
ANDREA | E0020C | ELEC | DEM | DSL_STRBCKS_DEM
ANDREA | E0023 | ELEC | PULSE |  | ROV_A_KWH
ANDREA | E0025 | ELEC | DEM | MG.DEM
MICHAEL | E0026 | ELEC | DEM | NA_DEM
MICHAEL | E0028 | ELEC | DEM | THAGARD_KW
OMAR | E0030 | ELECPRO | SQUARE D | LIFE_SQUARE_D1
OMAR | E0030A | ELECPRO | DEM |  |  | DEM 2000 LOCATED IN TRANSFORMER EAST SIDE OF CUP
ANDREA | E0032 | ELEC | PULSE |  | LAKWH
OMAR | E0033 | ELECPRO | PULSE | SUBSTATION |  | NOT WORKING, VALUE =0
MICHAEL | E0035 | ELEC | PULSE |  | HOKWH | DEVICE IS READING ZERO. POSSIBLY BAD SENSOR.
ANDREA | E0036 | ELEC | DEM | OS_DEM
ANDREA | E0037 | ELEC | DEM | FISHER_DEM
ANDREA | E0038 | ELEC | DEM | 0038_MSB_M1
ANDREA | E0038A | ELEC | DEM | 0038_MSB_M2
ANDREA | E0039 | ELEC | DEM | 0039-KW-ENERGY
ANDREA | E0040 | ELEC | DEM | 0040_DEM
MICHAEL | E0041 | ELEC | DEM | KE_DEM_KW
MICHAEL | E0042 | ELEC | PULSE |  | NUKWH
ANDREA | E0042A | ELEC | DEM | NU_DEM
MICHAEL | E0044 | ELEC | DEM | RO_DEM
ANDREA | E0045 | ELEC | DEM | RI_DEM
MICHAEL | E0046 | ELEC | DEM | SH_B_DEM
ANDREA | E0047 | ELEC | DEM | LLDEM
MICHAEL | E0050 | ELEC | DEM | STN_DEM
ANDREA | E0052 | ELEC | PULSE |  | ROV_B_KWH
MICHAEL | E0054 | ELEC | DEM | 0054_NM_DEM
ANDREA | E0055 | ELEC | DEM | ED_DEM
MICHAEL | E0057 | ELEC | PULSE |  | PBKWH
MICHAEL | E0070 | ELEC | DEM | PG_800amp
MICHAEL | E0070A | ELEC | CALCULATED |  | PGKA50, PGKA51, PGKA29, PGKA30, PGKA31
MICHAEL | E0070B | ELEC | DEM | PGEM01 |  | VIRTUAL POINT CREATED PGKW01 FOR DEVICE. PPCL NEEDS TO BE UPDATED
MICHAEL | E0070D | ELEC | DEM | PGEM03 |  | VIRTUAL POINT CREATED PGKW03 FOR DEVICE. PPCL NEEDS TO BE UPDATED
MICHAEL | E0070E | ELEC | DEM | PGEM04
MICHAEL | E0072 | ELEC | DEM | LO_DEM
MICHAEL | E0074 | ELEC | DEM | LANDIS_DEM1
MICHAEL | E0074A | ELEC | DEM | LANDIS_DEM2
MICHAEL | E0074B | ELEC | VIRTUAL |  |  | CALCULATED USING E0074,E0074A
MICHAEL | E0075 | ELEC | DEM | MH_MDP
ANDREA | E0075B | ELEC | DEM | MC_SP
ANDREA | E0075C | ELEC | DEM | MC_LG
MICHAEL | E0076 | ELEC | PULSE | PSKWH
MICHAEL | E0077 | ELEC | DEM | MA_DEM
MICHAEL | E0079 | ELEC | DEM | TCKWLAN
MICHAEL | E0085 | ELEC | DEM | 0085_CAWBKW
TJ | E0089 | ELEC | DEM | MS_DEM
MICHAEL | E0091 | ELEC | DEM | HPL_DEM
MICHAEL | E0091A | ELEC | IGNORE | N/A | N/A | MANUAL READ
MICHAEL | E0091B | ELEC | VIRTUAL |  |  | HPL_DEM, E0091A
MICHAEL | E0091C | ELEC | DEM | SP1-TRACK-DEM |  | DEVICE IS SHOWING FAILED
MARCELA | E0100 | ELEC | SQUARE D | M1517, M1523 | 0200_M15-17_KW, 0200_M15-23_KW
MICHAEL | E0100B | ELEC | CALCULATED |  |  | PHB_LVL1_1LA, PHB_LVL1_1LB
MICHAEL | E0100C | ELEC | DEM | PHA_FLD__LHTS_DEM
MICHAEL | E0100D | ELEC | DEM | UCC_FIELD_LGT
MICHAEL | E0100E | ELEC | DEM | UC2000
MICHAEL | E0100F | ELEC | DEM | UC2400
MICHAEL | E0100G | ELEC | DEM | UC2500 |  | DEVICE IS SHOWING FAILED
MARCELA | E0100H | ELEC | VIRTUAL
MICHAEL | E0100J | ELEC | IGNORE | N/A | N/A | METER NO LONGER BEING USED. PPCL IS DISABLED
MARCELA | E0100K | ELEC | DEM | DI_NODEKW, LANDIS_DEM1, DIRAC_DEM
MICHAEL | E0100L | ELEC | DEM | PHA_CN_DEM
MICHAEL | E0100M | ELEC | DEM | MEDIA_DEM |  | DEM SHOWING DISCONNECTED AND FAILED
MICHAEL | E0100M1 | ELEC | DEM | AT&T3 |  | DEM SHOWING DISCONNECTED AND FAILED
MICHAEL | E0100M2 | ELEC | VIRTUAL |  |  | MEDIA_DEM, AT&T3
MICHAEL | E0100N | ELEC | DEM | PHB_DEM_GG |  | DEM SHOWING DISCONNECTED AND FAILED
MICHAEL | E0100P | ELEC | DEM | AT&T0
MICHAEL | E0100Q | ELEC | DEM | AT&T2 |  | DEM SHOWING DISCONNECTED AND FAILED
MARCELA | E0100R | ELEC | DEM | PHB_DEM_FT
ANDREA | E0113 | ELEC | PULSE |  | CAKWH
ANDREA | E0113A | ELEC | PULSE |  | CAKWHA
ANDREA | E0114 | ELEC | DEM | ENGLAB_DEM
ANDREA | E0115 | ELEC | DEM | HOW_KWH
ANDREA | E0115A | ELEC | DEM | BB_SCOREBOARD
MARCELA | E0116 | ELEC | DEM | LV_DEM |  | APP 721
MARCELA | E0116A | ELEC | DEM | NWDEM1 |  | APP 719
MARCELA | E0116B | ELEC | DEM | NWDEM2 |  | APP 2675
MICHAEL | E0117 | ELEC | DEM | CIRCUS_METER |  | DEM SHOWING DISCONNECTED
ANDREA | E0121 | ELEC | DEM | 0121-KW-ENERGY
ANDREA | E0122_CELLTWR | ELEC | DEM | SP1-VERIZON-DEM
ANDREA | E0132 | ELEC | DEM | TG_KW
ANDREA | E0134 | ELEC | DEM | SN_DEM
ANDREA | E0134A | ELEC | DEM | SS_DEM
ANDREA | E0134B | ELEC | DEM | SS_STARBUCKS.DEM
ANDREA | E0134C | ELEC | VIRTUAL |  |  | CALCULATED USING E0134, E0134A & E0134B
ANDREA | E0135 | ELEC | DEM | SA_DEM
MICHAEL | E0146 | ELEC | DEM | IMDEM
MARCELA | E0223A | ELEC | DEM | UCU-SEL-SOUTH:KW.17E | 0200_M15-17E_KW | APP 11606
MARCELA | E0223A1 | ELEC | DEM | PHA_A0000
MARCELA | E0223A2 | ELEC | VIRTUAL
MARCELA | E0223B | ELEC | DEM | UCU-SEL-SOUTH:KW.17C | 0200_M15-17C_KW | APP 11606
MARCELA | E0223B1 | ELEC | DEM | AT&T1 |  | FAILED
MARCELA | E0223B2 | ELEC | IGNORE |  |  | NOT NEEDED
MARCELA | E0223B3 | ELEC | VIRTUAL
MARCELA | E0223B4 | ELEC | DEM | PHA_A171
MARCELA | E0223B5 | ELEC | DEM | SKY_BOX |  | APP 719
MARCELA | E0223B6 | ELEC | DEM | VERIZON_DEM |  | FAILED
MARCELA | E0223C | ELEC | IGNORE |  |  | NOT NEEDED
MARCELA | E0224A | ELEC |  |  |  | NOT FOUND. UCB ELEVATOR, NARIMAN'S GRAPHICS ALL HAVE THIS DATA POINT EMPTY. HOWEVER, IT IS BEING CHARGED IN AIM.
MARCELA | E0224B | ELEC | DEM | PHB_LVL13 |  | APP 721
MARCELA | E0224B1 | ELEC | CALCULATED | UCB_CHW_P1VFD, UCB_CHW_P2VFD, UCB_HHW_P1VFD, UCB_HHW_P2VFD
MARCELA | E0224B2 | ELEC | DEM | SLVL3D | SLV3KW | APP 710. Point is the one actually being reported. I'm unsure how the point gets its value. The meter dumps it's value into point 0224_LVL3_KW32.
MARCELA | E0224B3 | ELEC | VIRTUAL
MARCELA | E0224B6 | ELEC | DEM | AHU346_DEM, LA-LC_DEM, KITCH_DEM |  | APP 717
MARCELA | E0224C | ELEC | DEM | PHB_LVL47 |  | APP 721
MARCELA | E0224C1 | ELEC | DEM | SLVL4D | SLV4KW | APP 710. Point is the one actually being reported. I'm unsure how the point gets its value.
MARCELA | E0224C2 | ELEC | VIRTUAL
MARCELA | E0224C3 | ELEC | DEM | 0224_UCB_SCORE_BD |  | APP 2676
MARCELA | E0224C4 | ELEC | DEM | SLV5D1 |  | E0224C4 AND E0224C5 are added for billing. Not sure what ratio or rationale is used to split bill.
MARCELA | E0224C5 | ELEC | DEM | SLV5D2 |  | E0224C4 AND E0224C5 are added for billing. Not sure what ratio or rationale is used to split bill.
MARCELA | E0224C6 | ELEC | DEM | 0024_UCB_RIBBION |  | APP 2673
MARCELA | E0224D | ELEC | DEM | UCB_DEM_MAIN |  | APP 2677
MARCELA | E0225A | ELEC | DEM | PHC_DEM_C170 |  | THIS METERID IS NOT CHARGED IN AIM, BUT THE DATA PROVIDES CHARGES FOR E0225A1.
MARCELA | E0225A1 | ELEC | DEM | PHC_C170 |  | DISCONNECTED. THIS IS THE METERID CHARGED IN AIM, BUT THE DATA IS COMING FROM METER E0225A.
MARCELA | E0225A2 | ELEC | VIRTUAL
MARCELA | E0225A3 | ELEC | DEM | AT&T4 |  | APP 717
MARCELA | E0225A4 | ELEC | DEM | UCC_SKYBX_DAIKIN |  | APP 718
MARCELA | E0225B | ELEC | DEM | PHC_DEM_C171 |  | THIS METERID IS NOT CHARGED IN AIM, BUT THE DATA PROVIDES CHARGES FOR E0225B1.
MARCELA | E0225B1 | ELEC | DEM | PHC_C171 |  | DISCONNECTED. THIS IS THE METERID CHARGED IN AIM, BUT THE DATA IS COMING FROM METER E0225B.
MARCELA | E0225B2 | ELEC | VIRTUAL
MARCELA | E0226 | ELEC | DEM | CM_DEM |  | APP 721
MARCELA | E0226A | ELEC | SQUARE D | UC1700 |  | READING ZERO. TRUNK_3_NODE_29 PROGRAM HAS A LOT OF UNDEFINED/DISABLED LINES.
MARCELA | E0226B | ELEC | DEM | SKYBX_DEM |  | APP 719
MARCELA | E0226C | ELEC | DEM | CM_DEM_KIT1, CM_DEM_KIT2, CM_DEM_KIT3, 0226_AH11_DEM |  | 3 FIRST ONES ARE FAILED
MARCELA | E0226D | ELEC | VIRTUAL
MICHAEL | E0240 | ELEC | DEM | BAND_FIELD |  | DEM SHOWING DISCONNECTED
MICHAEL | E0260 | ELEC | DEM | LIDEM
MICHAEL | E0293 | ELEC | DEM | HWDM
MICHAEL | E0378 | ELEC | DEM | PG2_DEM1
PATRICK | E0379 | ELEC | DEM | SV_DEM_MSB |  | FAILED
PATRICK | E0379A | ELEC | DEM | SV_DEM_H1
PATRICK | E0379B | ELEC | DEM | SV_DEM_24HR_DINER
PATRICK | E0379C | ELEC | DEM | SV_DEM_H2
PATRICK | E0379D | ELEC | DEM | SV_DEM_H3
PATRICK | E0379E | ELEC | CALCULATED | SV_DEM_MSB, SV_DEM_H1, SV_DEM_24HR_DINER, SV_DEM_H2, SV_DEM_H3
MICHAEL | E0385 | ELEC | DEM | WS_DEM
TJ | E0488 | ELEC | DEM | WDINING_DEM
TJ | E0495 | ELEC | DEM | 0495-KW-ENERGY |  | APP 11996
TJ | E0496 | ELEC | DEM | 0496-KW-ENERGY |  | APP 11996
TJ | E0497 | ELEC | DEM | 0497-KW-ENERGY |  | APP 11996
TJ | E0498 | ELEC | DEM | 0498-KW-ENERGY |  | APP 11996
MICHAEL | E0904 | ELEC | IGNORE | N/A | N/A | MANUAL READ
MICHAEL | E0904A | ELEC | IGNORE | N/A | N/A | MANUAL READ
TJ | E4001 | ELEC | DEM | MED_SCH_DEM1
TJ | E4002 | ELEC | DEM | MED_SCH_DEM2
TJ | E4004 | ELEC | DEM | PSY_DEM
TJ | E4006 | ELEC | DEM | PG3DEM
PATRICK | E4007 | ELEC | SQUARE D | LIFE_SQUARE_D1 |  | FAILED
PATRICK | E4007B | ELEC | SQUARE D | LIFE_SQUARE_D2
TJ | E4008 | ELEC | DEM | CHEM_DEM02
TJ | E4008B | ELEC | DEM | CHEM_DEM03
TJ | E4009 | ELEC | DEM | CLASS_DEM1 |  | APP 722
MARCELA | E4010 | ELEC | DEM | 4010-KW-ENERGY |  | APP 10301, DENT PS3037
MICHAEL | E4011 | ELEC | DEM | STSC_DEM1
MICHAEL | E4014 | ELEC | DEM | PG4DEM
MARCELA | E4018 | ELEC | DEM | 4018_MSB1_DEM, 4018_MSB2_DEM, 4018_MSB1_METER, 4018_MSB2_METER, 4018_EMER_LGHT_PWM, 4018_HVAC_PWM, 4018_LEGALLY_REQ_PWM, 4018_LIGHTING_PWM, 4018_RECEPTACLES_PWM, 4018_STANDBY_PWM, 4018_MB3_PWM |  | UNION. MSB1 AND MSB2 METER ARE APP 11624.
MARCELA | E4018A | ELEC | DEM | 4018_BOOKSTORE_PWM |  | BOOKSTORE
MARCELA | E4018B | ELEC | DEM | 4018_CATKIT_OSB_PWM, 4018_CATKIT_PWM, 4018_PRODKIT_OSB_PWM, 4018_PRODKIT_PWM, 4018_PROOF_OSB_PWM, 4018_TRADINGPOST_OSB_PWM, 4018_PANDA_PWM, 4018_PANERA_PWM, 4018_PIZZA_PWM, 4018_POLLO_PWM, 4018_PROOF_PWM, 4018_STARBUCKS_PWM, 4018_TRADINGPOST_PWM, 4018_BUS_SERV_STBY_PWM, 4018_BUSINESS_SERV_PWM, 4018_PANDA_OSB_PWM, 4018_PANERA_OSB_PWM, 4018_PIZZA_OSB_PWM, 4018_POLLO_OSB_PWM, 4018_STARBUCKS_OSB_PWM |  | FOOD SERVICE COMBINED. EACH LOCATION HAS ONE PWM AND ONE STDBY/OSB PWM.
MICHAEL | E4020 | ELEC | DEM | WILD_S_DEM
MICHAEL | E4021 | ELEC | DEM | WILD_N_DEM
MICHAEL | E4022 | ELEC | DEM | WILD_3_DEM-1
MICHAEL | E4025 | ELEC | DEM | PG5_DEM
MARCELA | E4029 | ELEC | DEM | JBA_DEMMAIN
MARCELA | E4029A | ELEC | DEM | JBA_DEMSECFA, JBA_DEMCFA, JBA_DEMAH12, JBA_DEML1, JBA_DEML1A, JBA_DEMAH21
MARCELA | E4029B | ELEC | DEM | JBA_DEMSERR, JBA_DEMRR, JBA_DEMAH13, JBA_DEML1, JBA_DEML1A, JBA_DEMAH21
MARCELA | E4029C | ELEC | DEM | JBA_DEMSEPOD, JBA_DEML1, JBA_DEML1A
MARCELA | E4029D | ELEC | VIRTUAL
PATRICK | E4030 | ELEC | DEM | WEL_MAINSWBD
MARCELA | E4030 | ELEC | DEM | WEL_MAINSWBD |  | APP 723
MARCELA | E4030A | ELEC | VIRTUAL |  |  | GSF BASED. USES E4030.
MARCELA | E4030B | ELEC | VIRTUAL |  |  | GSF BASED. USES E4030.
MARCELA | E4030C | ELEC | VIRTUAL |  |  | GSF BASED. USES E4030.
MARCELA | E4030D | ELEC | VIRTUAL |  |  | GSF BASED. USES E4030.
MARCELA | E4031 | ELEC | DEM | STSC_S_DEM |  | APP 721
MARCELA | E4060 | ELEC | DEM | 4060_MAINSWITCHGEAR |  | APP 723
MARCELA | E4061 | ELEC | DEM | 4061_MAINSWITCHGEAR |  | APP 723
MARCELA | E4062 | ELEC | DEM | 4062_MAINDEM |  | APP 2677
MARCELA | E4062A | ELEC | DEM | 4062_FSATSDEM |  | #COM
MARCELA | E4063 | ELEC | DEM | 4063_MAINDEM |  | APP 2677
MICHAEL | E4090 | ELEC | DEM | IFPF_DEM
MARCELA | EP0100A | ELECPRO | DEM | UCU-SEL-SOUTH:KW.23C | 0200_M15-23C_KW | APP 11606
MARCELA | EP4013 | ELECPRO | SQUARE D | M1522
MARCELA | EPU001 | ELECPRO | DEM | PLANT3_NEW_COND_PMPS |  | app 719
MARCELA | HW4018 | HW | BTU | 4018_HW_BTU_METER
MARCELA | PCW4018 | PCHW | BTU | 4018_PCHW_BTU_METER
PATRICK | ST0000 | STEAM | CALCULATED |  | B3SFLO, CUP_STMHDRPRS, B1SFLO, CUP_B2STMFLW, CUP_B2STMPRS
PATRICK | ST0001 | STEAM | CALCULATED |  | WE_SFLO, WE_STH | WE_STH READING INCORRECT
PATRICK | ST0002 | STEAM | MASS FLOW |  | DISFLW
PATRICK | ST0003 | STEAM | CALCULATED |  | WISTFL, WISTH | WISTH READING INCORRECT
PATRICK | ST0004 | STEAM | MASS FLOW |  | DHSFLW
PATRICK | ST0005 | STEAM | CALCULATED |  | EPS_STEAMSF, EPS_STEAMHIP
PATRICK | ST0006 | STEAM | MASS FLOW |  | PRSFLW
PATRICK | ST0007 | STEAM | MASS FLOW |  | FA_SFLW
PATRICK | ST0008 | STEAM | CALCULATED |  | BESTFL, BESTP1
PATRICK | ST0009 | STEAM | MASS FLOW |  | 0009_STEAM_FLO
PATRICK | ST0012 | STEAM | CALCULATED |  | 0012_SFLO, 0012_HPS
PATRICK | ST0013 | STEAM | CALCULATED |  | 0013_SFLO, 0013_HPS
PATRICK | ST0014 | STEAM | MASS FLOW |  | 0014_STMFLO
PATRICK | ST0015 | STEAM | MASS FLOW |  | BRSFLO
PATRICK | ST0016 | STEAM | MASS FLOW |  | GHSFLO
PATRICK | ST0017A | STEAM | CALCULATED |  |  | MANUALLY CALCULATED BY NARIMAN.
PATRICK | ST0017B | STEAM | CALCULATED |  | JO_HPSP, JO_SFLO
PATRICK | ST0017C | STEAM | CALCULATED |  | JO_HPSP, JO_SFLO
PATRICK | ST0017D | STEAM | CALCULATED |  | JB_STM_FLW, JB_STM_HPS
PATRICK | ST0019 | STEAM | CALCULATED |  | LS_SFLO | STEAM DENSITY SET TO 0.26
PATRICK | ST0020 | STEAM | MASS FLOW |  | SCSFLW
PATRICK | ST0025 | STEAM | CALCULATED |  | MGSFLO | STEAM DENSITY SET TO 0.21
PATRICK | ST0026 | STEAM | CALCULATED |  | NASFLO, NAHP1, NASTH, NASFLD, NASFLP | USES HWP 1 ON OFF TO ZERO READING ON NAST32
PATRICK | ST0028 | STEAM | CALCULATED |  | HCSFLO | STEAM DENSITY SET TO 0.26
PATRICK | ST0035 | STEAM | CALCULATED |  | HOSFLO | STEAM DENSITY SET TO 0.21
PATRICK | ST0036 | STEAM | MASS FLOW |  | OSSFLO
PATRICK | ST0037 | STEAM | MASS FLOW |  | 0037.FL.AHU13-14.FLSFLO
PATRICK | ST0038 | STEAM | MASS FLOW |  | DTSFLO
PATRICK | ST0039 | STEAM | MASS FLOW |  | 0039_HHW_MPSF
PATRICK | ST0040 | STEAM | CALCULATED |  | 0040_HPSFLO, 0040_HPSP
PATRICK | ST0041 | STEAM | CALCULATED |  | KESFLO_ | STEAM DENSITY DONE THROUGH SCRIPTING "B2SD"
PATRICK | ST0042 | STEAM | MASS FLOW |  | NUSFLW
PATRICK | ST0044 | STEAM | CALCULATED |  | ROG_SFLO, ROG_HPS
PATRICK | ST0045 | STEAM |  |  | NU_PHWST, RI_PHWRT, RI_PHWFLOW
PATRICK | ST0046 | STEAM | CALCULATED |  | SH_STM_HPF, SH_STM_HPP
PATRICK | ST0050 | STEAM | MASS FLOW |  | STN_SFLO
PATRICK | ST0052 | STEAM | CALCULATED |  | ROV_B_STMF, ROV_B_STMH
PATRICK | ST0054 | STEAM | MASS FLOW |  | 0054_SFLO
PATRICK | ST0055 | STEAM | MASS FLOW |  | 0055_STFLO_LBM
PATRICK | ST0057 | STEAM | CALCULATED |  | PBSTFL | STEAM DENSITY DONE THROUGH SCRIPTING "B2SD"
PATRICK | ST0070 | STEAM | CALCULATED |  | PGSTF | ODD FORMULA PGSFLW = PGSTF * 0.22
PATRICK | ST0070A | STEAM | IGNORE | N/A | N/A | MANUALLY CALCULATED BY NARIMAN.
PATRICK | ST0070B | STEAM | CALCULATED |  | PGSTF | ODD FORMULA PGSFLW = PGSTF * 0.22
PATRICK | ST0072 | STEAM | MASS FLOW |  | LOSFLO
PATRICK | ST0074 | STEAM | CALCULATED |  | LANDIS_HPSF, LANDIS_HPSP
PATRICK | ST0075 | STEAM | CALCULATED |  | MH_STFL | STEAM DENSITY SET TO 0.25
PATRICK | ST0076 | STEAM | CALCULATED |  | PSSFLO | ODD FORMULA PSSFLW = PSSFLO * 0.6799999
PATRICK | ST0077 | STEAM | CALCULATED |  | MASFLO | STEAM DENSITY DONE THROUGH SCRIPTING "B2SD"
PATRICK | ST0085 | STEAM | MASS FLOW |  | CAWHPSF
PATRICK | ST0089 | STEAM | MASS FLOW |  | MS_SFLW
PATRICK | ST0091 | STEAM | CALCULATED |  | HPL_STMFLO, HPL_STMHPSP
PATRICK | ST0113 | STEAM | CALCULATED |  | CASFLO | STEAM DENSITY SET TO 0.22
PATRICK | ST0116 | STEAM | CALCULATED |  | LV_SFLO | STEAM DENSITY SET TO 0.2, AND IN CAROTHERS BUILDING?
PATRICK | ST0116A | STEAM | CALCULATED |  | NWHPSF | STEAM DENSITY DONE THROUGH SCRIPTING "B2SD"
PATRICK | ST0116B | STEAM | CALCULATED |  | NWHPSF | STEAM DENSITY 0116_NWS_STMD is not calculated
PATRICK | ST0116C | STEAM | CALCULATED |  | NWHPSF | STEAM DENSITY 0116_NWS_STMD is not calculated
PATRICK | ST0121 | STEAM | MASS FLOW |  | 0121_ROTC_STM_FLOW
PATRICK | ST0132 | STEAM | MASS FLOW |  | TGSFLO
PATRICK | ST0134 | STEAM | MASS FLOW |  | SN_SFLW
PATRICK | ST0134A | STEAM | MASS FLOW |  | SS_STF1
PATRICK | ST0135 | STEAM | CALCULATED |  | SASTFL | STEAM DENSITY SET TO 0.22
PATRICK | ST0146 | STEAM | MASS FLOW |  | IMSHF
PATRICK | ST0223 | STEAM | MASS FLOW |  | AHPSFL
PATRICK | ST0223A | STEAM | CALCULATED | UCB_HHW_BTU_WEST, UCB_HHW_BTU_EAST | AHPSFL, "UCB_HHW_BLD_HWS, ucb_hhw_bld_hwr, UCB_HHW_BLD_HWF, CMSFLO, CMLPSP | CMLPSP IS LOW PSI STEAM
PATRICK | ST0224 | STEAM | CALCULATED | UCB_HHW_BTU_WEST | UCB_HHW_BLD_HWS, ucb_hhw_bld_hwr, UCB_HHW_BLD_HWF
PATRICK | ST0224TWS | STEAM | CALCULATED | UCB_HHW_BTU_EAST, UCB_HHW_BTU_WEST
PATRICK | ST0226 | STEAM | CALCULATED |  | CMSFLO, CMLPSP | DENSITY SET BY LOW PSI STEAM
PATRICK | ST0260 | STEAM | MASS FLOW |  | LISFLO
PATRICK | ST0379 | STEAM | CALCULATED |  | SV_HPSFLW
PATRICK | ST0379A | STEAM | CALCULATED | SV_FTU_RM108, SV_FTU_RM112, SV_FTU_RM116, SV_FTU_RM118, SV_FTU_RM120, SV_FTU_RM121, SV_FTU_RM125, SV_FTU_RM127, SV_FTU_RM135, SV_FTU_RM141
PATRICK | ST0379B | STEAM | CALCULATED | SV_FTU_RM300B, SV_FTU_RM300C, SV_FTU_RM301, SV_FTU_RM303, SV_FTU_RM307, SV_FTU_RM308, SV_FTU_RM309, SV_FTU_RM314, SV_FTU_RM317, SV_FTU_RM321, SV_FTU_RM327, SV_FTU_RM332, SV_FTU_RM336, SV_FTU_RM340, SV_FTU_RM343, SV_FTU_RM346, SV_FTU_RM349, SV_FTU_RM352E, SV_FTU_RM352W, SV_FTU_RM353, SV_FTU_RM354
PATRICK | ST0379C | STEAM | CALCULATED | SV_FTU_RM208, SV_FTU_RM214, SV_FTU_RM215, SV_FTU_RM218, SV_FTU_RM219, SV_FTU_RM220, SV_FTU_RM221, SV_FTU_RM222 |  | VIRTUAL
PATRICK | ST0379D | STEAM | Mass Flow |  | SV_HPSFLW
PATRICK | ST0379E | STEAM | CALCULATED | SV_FTU_RM208, SV_FTU_RM214, SV_FTU_RM215, SV_FTU_RM218, SV_FTU_RM219, SV_FTU_RM220, SV_FTU_RM221, SV_FTU_RM222, SV_FTU_RM108, SV_FTU_RM112, SV_FTU_RM116, SV_FTU_RM118, SV_FTU_RM120, SV_FTU_RM121, SV_FTU_RM125, SV_FTU_RM127, SV_FTU_RM135, SV_FTU_RM141, SV_FTU_RM300B, SV_FTU_RM300C, SV_FTU_RM301, SV_FTU_RM303, SV_FTU_RM307, SV_FTU_RM308, SV_FTU_RM309, SV_FTU_RM314, SV_FTU_RM317, SV_FTU_RM321, SV_FTU_RM327, SV_FTU_RM332, SV_FTU_RM336, SV_FTU_RM340, SV_FTU_RM343, SV_FTU_RM346, SV_FTU_RM349, SV_FTU_RM352E, SV_FTU_RM352W, SV_FTU_RM353, SV_FTU_RM354 | SV_HPSFLW | VIRTUAL
PATRICK | ST0488 | STEAM | CALCULATED |  | WDINING_STMF | STEAM DENSITY DONE THROUGH SCRIPTING "B2SD"
PATRICK | ST0495 | STEAM | CALCULATED |  | REAHPSF, REAHPSP
PATRICK | ST0496 | STEAM | CALCULATED |  | REBHPSF, REBHPSP
PATRICK | ST0497 | STEAM | CALCULATED |  | RECHPSF, RECHPSP
PATRICK | ST0498 | STEAM | CALCULATED |  | REDHPSF, REDHPSP
PATRICK | ST4001 | STEAM | CALCULATED |  | MED_SCH_HPSF, MED_SCH_HPSP
PATRICK | ST4004 | STEAM | CALCULATED |  | PSY_HPSF, PSY_HPSP
PATRICK | ST4007 | STEAM | CALCULATED |  | LIFE_HPSF, LIFE_HPSP
PATRICK | ST4008 | STEAM | CALCULATED |  | CHEM_HPSF, CHEM_HPSP
PATRICK | ST4009 | STEAM | CALCULATED |  | CLASS_SFLO, CLASS_HPSP
PATRICK | ST4011 | STEAM | CALCULATED |  | STSC_HPSF, STSC_HPSP
PATRICK | ST4020 | STEAM | CALCULATED |  | WILD_S_HPSF, WILD_S_HPSP
PATRICK | ST4021 | STEAM | CALCULATED |  | WILD_N_HPSF, WILD_N_HPSP
PATRICK | ST4022 | STEAM | CALCULATED |  | WILD_3_STM_FLOW1/3, WILD_3_STM_HPS | WILD_3_STM_FLOW1_3 IS HOW DESIGO DISPLAYS NAME
PATRICK | ST4029 | STEAM | CALCULATED |  | JBA_SFLO, JBA_STEAM.PRESSURE
PATRICK | ST4029A | STEAM | CALCULATED |  | JBA_SFLO, JBA_STEAM.PRESSURE,
PATRICK | ST4029B | STEAM | CALCULATED |  | JBA_SFLO, JBA_STEAM.PRESSURE
PATRICK | ST4029C | STEAM | CALCULATED |  | JBA_SFLO, JBA_STEAM.PRESSURE
PATRICK | ST4029D | STEAM | CALCULATED |  | JBA_SFLO, JBA_STEAM.PRESSURE
PATRICK | ST4029E | STEAM | CALCULATED |  | JBA_SFLO, JBA_STEAM.PRESSURE
PATRICK | ST4030 | STEAM | CALCULATED |  | WEL_SFLO, WEL_HPS
PATRICK | ST4030A | STEAM | CALCULATED |  | WEL_SFLO, WEL_HPS
PATRICK | ST4030B | STEAM | CALCULATED |  | WEL_SFLO, WEL_HPS
PATRICK | ST4030C | STEAM | CALCULATED |  | WEL_SFLO, WEL_HPS
PATRICK | ST4030D | STEAM | CALCULATED |  | WEL_SFLO, WEL_HPS
PATRICK | ST4031 | STEAM | CALCULATED |  | STSC_S_HPSF, STSC_S_HPSP
PATRICK | ST4060 | STEAM | CALCULATED |  | 4060_SFLO, 4060_HPS
PATRICK | ST4061 | STEAM | CALCULATED |  | 4060_SFLO, 4060_HPS
PATRICK | ST4062 | STEAM | CALCULATED |  | 4062_SFLO, 4062_HPS
PATRICK | ST4062A | STEAM | BTU | 4062_HWBLD4BTU
PATRICK | ST4063 | STEAM | CALCULATED |  | 4062_SFLO, 4062_HPS
Total | 218 |  | 217 |  |  | 89
Note on G5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Both Degraff buildings receive a bill directly from CoT. Utility Type: ELT. MeterID for Degraff East: 105401EL.
Note on G6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Both Degraff buildings receive a bill directly from CoT. Utility Type: ELT. MeterID for Degraff West: 483233EL.
Note on E127: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: UNSURE. Substation is offline. Check points: "CITY-FSU_KW01" = "MAIN1_KW01" + "MAIN2_KW01" - "FSUKWH01"
Note on G378: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Yes, it’s still being billed in AiM.

## ELECTRICAL
UTILITIES BILLING |  |  |  | Pay attention to note |  | XX: JAN=33, FEB=34, MAR=35, APR=36, … , DEC=44
ELECTRICAL |  |  |  | Production meter |  | PX: points, e.g., P1, P2, P3 (for calculations, P1 is the first point name in the BAS POINT NAME column)
BLDG # | BLDG NAME | CUSTOMER | BILLED IN AIM (Y/N) | METER ID | METER TYPE | CALC | BAS POINT NAME(S) | NOTES | NEED ALIAS? (Y/N) | ALIAS | ALIAS IN DESIGO? (Y/N)
0000 |  | CAMPUS MASTER METER, FSUA32 + FSUB32 | N | E0000 | MASTER | SET EQUAL TO | MAIN2_KWXX |  | Y | E0000_UTL_METER_DAY32 | Y
0001 | WESTCOTT BUILDING | WESTCOTT BUILDING METER, WEKW32 | Y | E0001 | BUILDING | SET EQUAL TO | WE_KW32 |  | Y | E0001_UTL_METER_DAY32 | Y
0001 | WESTCOTT BUILDING | RUBY DIAMOND | Y | E0001A | BUILDING | SET EQUAL TO | RD_KW32 |  | Y | E0001A_UTL_METER_DAY32 | Y
0002 | DIFFENBAUGH BUILDING | DIFFENBAUGH BUILDING METER, DIKW32 | N | E0002 | DIST | SET EQUAL TO | DIKW32 |  | Y | E0002_UTL_METER_DAY32 | Y
0002 | DIFFENBAUGH BUILDING | DIFFENBAUGH NODE ROOM, DINKW32 | Y | E0002A | SUBMETER | SET EQUAL TO | DINKW32 |  | Y | E0002A_UTL_METER_DAY32 | Y
0002 | DIFFENBAUGH BUILDING | DIFFENBAUGH UPSTREAM METER FOR E0002 | Y | E0002B | VIRTUAL | SUBTRACT P1 - P2 | DIKW32, DINKW32 |  | N
0003 | WILLIAMS BUILDING | WILLIAMS BLDG METER, WIKW32 | N | E0003 | DIST | SET EQUAL TO | WIKW32 |  | Y | E0003_UTL_METER_DAY32 | Y
0003 | WILLIAMS BUILDING | WILLIAMS ATT CELL TOWER | Y | E0003A | SUBMETER | SET EQUAL TO | ATTKW32 |  | Y | E0003A_UTL_METER_DAY32 | Y
0003 | WILLIAMS BUILDING | WILLIAMS UPSTREAM METER | Y | E0003B | VIRTUAL | SUBTRACT P1 - P2 | WIKW32, ATTKW32 |  | N
0004 | DODD HALL | DODD HALL&AUD., DHKW32 | Y | E0004 | BUILDING | SET EQUAL TO | DH_KW32 |  | Y | E0004_UTL_METER_DAY32 | Y
0005 | CRIMINOLOGY AND CRIMINAL JUSTICE BUILDING | EPPES HALL, (OLD PSY), POKW32 | Y | E0005 | BUILDING | SET EQUAL TO | POKW32 |  | Y | E0005_UTL_METER_DAY32 | Y
0006 | KELLOGG BUILDING | KELLOGG RES., PRKW32 | Y | E0006 | BUILDING | SET EQUAL TO | PRKW32 |  | Y | E0006_UTL_METER_DAY32 | Y
0007 | FINE ARTS BUILDING | FINE ARTS, FAKW32 | Y | E0007 | BUILDING | SET EQUAL TO | FA_KW32 |  | Y | E0007_UTL_METER_DAY32 | Y
0008 | BELLAMY BUILDING | BELLAMY BUILDING, BEKW32 | N | E0008 | DIST | SET EQUAL TO | BE_KW32 |  | Y | E0008_UTL_METER_DAY32 | Y
0008 | BELLAMY BUILDING | BELLAMY CELL TOWER, | Y | E0008A | SUBMETER | SET EQUAL TO | BELL_CELL_KW32 |  | Y | E0008A_UTL_METER_DAY32 | Y
0008 | BELLAMY BUILDING | BELLAMY UPSTREAM METER | Y | E0008B | VIRTUAL | SUBTRACT P1 - P2 | BE_KW32, BELL_CELL_KW32 |  | N
0009 | BIOMEDICAL RESEARCH FACILITY | BIOMED, BMKW32 | Y | E0009 | BUILDING | SET EQUAL TO | 0009_KW_32 |  | Y | E0009_UTL_METER_DAY32 | Y
0010 | TURNBULL CONFERENCE CENTER | CPD | Y | E0010A | BUILDING | SET EQUAL TO | CONF_KW32 |  | Y | E0010A_UTL_METER_DAY32 | Y
0011 | SHAW BUILDING (MAIN CAMPUS) | SHAW BUILDING-NEW, SHAW_KW32 | N | E0011 | DIST | SET EQUAL TO | SHAW_KW32 |  | Y | E0011_UTL_METER_DAY32 | Y
0011 | SHAW BUILDING (MAIN CAMPUS) | SHAW BLDG SPRINT NODE RM., SHKA32 | Y | E0011B | SUBMETER | SET EQUAL TO | SHKA32 |  | Y | E0011B_UTL_METER_DAY32 | Y
0011 | SHAW BUILDING (MAIN CAMPUS) | SHAW BLDG, E&G UPSTREAM METER | N | E0011C | VIRTUAL | SUBTRACT P1 - P2 | SHAW_KW32, SHKA32 |  | N
0012 | JENNIE MURPHREE HALL | JENNIE MURPHREE HALL, JMKW32 | Y | E0012 | BUILDING | SET EQUAL TO | 0012_KW32 |  | Y | E0012_UTL_METER_DAY32 | Y
0013 | REYNOLDS HALL | REYNOLDS HALL, RHKW32 | Y | E0013 | BUILDING | SET EQUAL TO | 0013_KW32 |  | Y | E0013_UTL_METER_DAY32 | Y
0014 | BRYAN HALL | BRYAN HALL, BHKW32 | Y | E0014 | BUILDING | SET EQUAL TO | 0014_KW32 |  | Y | E0014_UTL_METER_DAY32 | Y
0015 | BROWARD HALL | BROWARD HALL | Y | E0015 | BUILDING | SET EQUAL TO | BRKW32 |  | Y | E0015_UTL_METER_DAY32 | Y
0016 | GILCHRIST HALL | GILCHRIST HALL, GHKW32 | Y | E0016 | BUILDING | SET EQUAL TO | GHKW32 |  | Y | E0016_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON, DINING- FOOD SVR, JO_KW | N | E0017C | DIST | SET EQUAL TO | JO_KW32 |  | Y | E0017C_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON, DINING E&G, JO_TENKW | Y | E0017D | SUBMETER | SET EQUAL TO | JO_TENKW32 |  | Y | E0017D_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON, DINING E&G EMER ELEC | N | E0017E | SUBMETER | EMPTY | EMPTY | NOT NEEDED | N
0017 | JOHNSTON BUILDING | JOHNSTON, DINING UPSTREAM | Y | E0017F | VIRTUAL | SUBTRACT P1 - P2 | JO_KW32, JO_TENKW32 |  | N
0017 | JOHNSTON BUILDING | JOHNSTON, NEW SECTION | Y | E0017G | BUILDING | SET EQUAL TO | JB_KW32 |  | Y | E0017G_UTL_METER_DAY32 | Y
0019 | SHORES BUILDING | LOUIS SHORES LIB. LSKW32 | Y | E0019 | BUILDING | SET EQUAL TO | LS_KW32 |  | Y | E0019_UTL_METER_DAY32 | Y
0020 | DIRAC SCIENCE LIBRARY | DIRAC BLDG METER, SCKW32 | N | E0020 | DIST | SET EQUAL TO | DIRAC_KW32 |  | Y | E0020_UTL_METER_DAY32 | Y
0020 | DIRAC SCIENCE LIBRARY | DIRAC NODE ROOM, SCKW32 | Y | E0020A | SUBMETER | SET EQUAL TO | SCKB32 |  | Y | E0020A_UTL_METER_DAY32 | Y
0020 | DIRAC SCIENCE LIBRARY | DIRAC STARBUCKS | Y | E0020C | SUBMETER | SET EQUAL TO | DSL_SB_KW32 |  | Y | E0020C_UTL_METER_DAY32 | Y
0020 | DIRAC SCIENCE LIBRARY | DIRAC UPSTREAM METER | Y | E0020B | VIRTUAL | SUBTRACT P1 - (P2+P3) | DIRAC_KW36, SCKB32, DSL_SB_KW32 |  | N
0023 | ROVETTA BUILDING A | BUSINESS NEW, ROVETTA A, BNWK32 | Y | E0023 | BUILDING | SET EQUAL TO | ROV_A_KW32 |  | Y | E0023_UTL_METER_DAY32 | Y
0025 | MONTGOMERY | MONTGOMERY GYM METER, MGKW32 | Y | E0025 | BUILDING | SET EQUAL TO | MGKW32 |  | Y | E0025_UTL_METER_DAY32 | Y
0026 | LEACH CENTER | LEACH-CAMPUS REC. NAKW32 | Y | E0026 | BUILDING | SET EQUAL TO | NAKW32 |  | Y | E0026_UTL_METER_DAY32 | Y
0028 | THAGARD BUILDING | THAGARD HEALTH CENTER, HCKW32 | Y | E0028 | BUILDING | SET EQUAL TO | HCKW32 |  | Y | E0028_UTL_METER_DAY32 | Y
0032 | COLLEGE OF LAW - B.K. ROBERTS HALL | BK ROBERTS LAW BLDG, LAWK32 | Y | E0032 | BUILDING | SET EQUAL TO | LAKW32 |  | Y | E0032_UTL_METER_DAY32 | Y
0035 | HOFFMAN TEACHING LAB | CHEMISTRY 2, HOFFMAN HOKW32 | Y | E0035 | DIST | SET EQUAL TO | 0035_KW32 |  | Y | E0035_UTL_METER_DAY32 | Y
0036 | ROGERS BUILDING (OSB) | OSB OCEANOGRAPHY, OSKW32 | Y | E0036 | SUBMETER | SET EQUAL TO | OS_KW32 |  | Y | E0036_UTL_METER_DAY32 | Y
0037 | FISHER LECTURE HALL | FISHER HALL | Y | E0037 | SUBMETER | SET EQUAL TO | FLKW32 |  | Y | E0037_UTL_METER_DAY32 | Y
0038 | DITTMER CHEMISTRY LAB | CHEMISTRY 1, DITMER METER A DTKA32 | Y | E0038 | BUILDING | SET EQUAL TO | 0038_M1_KW32 |  | Y | E0038_UTL_METER_DAY32 | Y
0038 | DITTMER CHEMISTRY LAB | CHEMISTRY 1, DITMER METER 2 DTKB32 | Y | E0038A | BUILDING | SET EQUAL TO | 0038_M2_KW32 |  | Y | E0038A_UTL_METER_DAY32 | Y
0039 | BIOLOGY UNIT I | BIOLOGY 1, BIKW32 | Y | E0039 | BUILDING | SET EQUAL TO | 0039_KW32 |  | Y | E0039_UTL_METER_DAY32 | Y
0040 | DUXBURY HALL | NURSING BLDG., NRKW32 | Y | E0040 | BUILDING | SET EQUAL TO | 0040_KW32 |  | Y | E0040_UTL_METER_DAY32 | Y
0041 | KEEN BUILDING | KEEN BLDG., KEKW32 | Y | E0041 | BUILDING | SET EQUAL TO | KEKW32 |  | Y | E0041_UTL_METER_DAY32 | Y
0042 | COLLINS RESEARCH BUILDING | NUCLEAR RESEARCH, SOUTH NUKA32 | Y | E0042 | BUILDING | SET EQUAL TO | 0042_KW32 |  | Y | E0042_UTL_METER_DAY32 | Y
0042 | COLLINS RESEARCH BUILDING | NUCLEAR NORTH PIT, NUKW32 | Y | E0042A | BUILDING | SET EQUAL TO | NUKA32 |  | Y | E0042A_UTL_METER_DAY32 | Y
0044 | ROGERS HALL | ROGERS HALL, ROKW32 | Y | E0044 | BUILDING | SET EQUAL TO | RO_KW32 |  | Y | E0044_UTL_METER_DAY32 | Y
0045 | RICHARDS BUILDING | RICHARDS BLDG. UPL, RIKW32 | Y | E0045 | BUILDING | SET EQUAL TO | RIKW32 |  | Y | E0045_UTL_METER_DAY32 | Y
0046 | SALLEY HALL | SALLEY HALL, SLKW32 | Y | E0046 | BUILDING | SET EQUAL TO | SH_KW32 |  | Y | E0046_UTL_METER_DAY32 | Y
0047 | COLLEGE OF LAW - RESEARCH CENTER (LIBRARY) | LAW LIBRARY, LLKW32 | Y | E0047 | BUILDING | SET EQUAL TO | LLKW32 |  | Y | E0047_UTL_METER_DAY32 | Y
0050 | STONE BUILDING | STONE BLDG., STKW32 | Y | E0050 | BUILDING | SET EQUAL TO | STN_KW32 |  | Y | E0050_UTL_METER_DAY32 | Y
0052 | ROVETTA BUILDING B | BUSINESS OLD, ROVETTA B, BWKW32 | Y | E0052 | BUILDING | SET EQUAL TO | ROV_B_KW32 |  | Y | E0052_UTL_METER_DAY32 | Y
0054 | HOUSEWRIGHT MUSIC BUILDING | MUSIC NORTH, HOUSEWRIGHT, NMKW32 | Y | E0054 | BUILDING | SET EQUAL TO | 0054_KW32 |  | Y | E0054_UTL_METER_DAY32 | Y
0055 | CAROTHERS HALL | EDUCATION, CAROTHERS & ENG LAB, EDKW32 | Y | E0055 | BUILDING | SET EQUAL TO | ED_KW32 |  | Y | E0055_UTL_METER_DAY32 | Y
0057 | PEPPER BUILDING | PEPPER BLDG., PBKW32 | Y | E0057 | BUILDING | SET EQUAL TO | PBKW32 |  | Y | E0057_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARKING GARAGE 1, PGKW32 | N | E0070 | DIST | SET EQUAL TO | PGKA32 |  | Y | E0070_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARK GARAGE #1, UPSTREAM METER | Y | E0070A | VIRTUAL | SUBTRACT P1 - (P2 + P3 + P4) | PGKW32, PGKB32, PGKD32, PGKE32 |  | N
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARK GARAGE #1, CARD CENTER, PGKB32 | Y | E0070B | SUBMETER | SET EQUAL TO | PGKB32 |  | Y | E0070B_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARK GARAGE #1, PGKD32 | Y | E0070D | SUBMETER | SET EQUAL TO | PGKD32 |  | Y | E0070D_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARK GARAGE #1, NEW FOOD SERVICES | Y | E0070E | SUBMETER | SET EQUAL TO | PGKE32 |  | Y | E0070E_UTL_METER_DAY32 | Y
0072 | LONGMIRE BUILDING | LONGMIRE BLDG., LOKW32 | Y | E0072 | BUILDING | SET EQUAL TO | LOKW32 |  | Y | E0072_UTL_METER_DAY32 | Y
0074 | LANDIS HALL | LANDIS HALL, LHKW32 | N | E0074 | DIST | SET EQUAL TO | LANDIS_KW32 |  | Y | E0074_UTL_METER_DAY32 | Y
0074 | LANDIS HALL | LANDIS HALL NODE ROOM, LHKA32 | Y | E0074A | SUBMETER | SET EQUAL TO | LANDIS_SPKW32 |  | Y | E0074A_UTL_METER_DAY32 | Y
0074 | LANDIS HALL | LANDIS HALL, UPSTREAM METER | Y | E0074B | VIRTUAL | SUBTRACT P1 - P2 | LANDIS_KW32, LANDIS_SPKW32 |  | N
0075 | MCCOLLUM HALL | MCCOLLUM HALL, MCKW32 | Y | E0075 | BUILDING | SET EQUAL TO | MH_KW32 |  | Y | E0075_UTL_METER_DAY32 | Y
0075 | MCCOLLUM HALL | MCCOLLUM HALL CELLTOWER, CL2KW32 | Y | E0075B | BUILDING | SET EQUAL TO | MC_SPKW32 |  | Y | E0075B_UTL_METER_DAY32 | Y
0075 | MCCOLLUM HALL | MCCOLLUM HALL, PARKING LOT MC_LGHT_KW32 | Y | E0075C | BUILDING | SET EQUAL TO | MC_LGKW32 |  | Y | E0075C_UTL_METER_DAY32 | Y
0076 | TANNER HALL | PUBLIC SAFTY, PSKW32 | Y | E0076 | BUILDING | SET EQUAL TO | PSKW32 |  | Y | E0076_UTL_METER_DAY32 | Y
0077 | MENDENHALL BUILDING A | MAINTENANCE A&B, MAKW32 | Y | E0077 | BUILDING | SET EQUAL TO | MAKW32 |  | Y | E0077_UTL_METER_DAY32 | Y
0079 | SPEICHER TENNIS CENTER | SPEICHER TENNIS CT., TCKW32 | Y | E0079 | BUILDING | SET EQUAL TO | SSTKW32 |  | Y | E0079_UTL_METER_DAY32 | Y
0085 | CAWTHON HALL | CAWTHON HALL, CAWKW32 | Y | E0085 | BUILDING | SET EQUAL TO | CAWKW32 |  | Y | E0085_UTL_METER_DAY32 | Y
0089 | KUERSTEINER MUSIC BUILDING | MUSIC SOUTH, KUERSTIENER, MSKW32 | Y | E0089 | BUILDING | SET EQUAL TO | MS_KW32 |  | Y | E0089_UTL_METER_DAY32 | Y
0091 | MCINTOSH TRACK & FIELD BUILDING | MIKE LONG TRACK BLDG., MANUAL READ | N | E0091 | DIST | SET EQUAL TO | HPL_KW32 |  | Y | E0091_UTL_METER_DAY32 | Y
0091 | MCINTOSH TRACK & FIELD BUILDING | MIKE LONG TRACK, EXT. METER, MANUAL READ | Y | E0091A | SUBMETER | MANUAL READ | MANK01 |  | Y | E0091A_UTL_METER_DAY32 | Y
0091 | MCINTOSH TRACK & FIELD BUILDING | MIKE LONG TRACK UPSTREAM METER | Y | E0091B | VIRTUAL | SUBTRACT P1 - P2 | HPL_KW32, MANK01 |  | N
0091 | MCINTOSH TRACK & FIELD BUILDING | TRACK/P. SOCCER/VOLLYBALL FIELD LIGHTS | Y | E0091C | BUILDING | SET EQUAL TO | TRACK_KW32 |  | Y | E0091C_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | STADIUM MASTER, UCKA+UCKB= UCKAB32 | N | E0100 | DIST | ADD P1 + P2 | 0200_M15-23_KW32, 0200_M15-17_KW32 |  | Y | E0100.1_UTL_METER_DAY32, E0100.2_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC SPORTS SHOP, UCKM32 | Y | E0100B | SUBMETER | SET EQUAL TO | UCB_SHOP_KW32 |  | Y | E0100B_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC EAST STANDS LIGHTS, UCKN32 | Y | E0100C | SUBMETER | SET EQUAL TO | PHA_FLKW32 |  | Y | E0100C_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC WEST STANDS LIGHTS, UCKU32 | Y | E0100D | SUBMETER | SET EQUAL TO | UCC_FLD_LGT_KW32 |  | Y | E0100D_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC ISLE 20, UCKO32 | Y | E0100E | SUBMETER | SET EQUAL TO | UCKO32 |  | Y | E0100E_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC TRAFFIC ISLE 9, UCKS32 | Y | E0100F | SUBMETER | SET EQUAL TO | UCKS32 |  | Y | E0100F_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC BOOSTERS CONCESSIONS, UCKT32 | Y | E0100G | SUBMETER | SET EQUAL TO | UCKT32 |  | Y | E0100G_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC UPSTREAM METER FOR E0100 | Y | E0100H | VIRTUAL | SUBTRACT DIST FROM ALL OTHER E0100 METERS, EXCEPT 0100K, 0100M1, 0100M2 | SUM(M15-23_KW32,M15-17_KW32) - SUM(UCKM32, PHA_FLKW32, PHC_FLKW32, UCKO32, UCKS32, UCKT32, UCKW32, PHA_CNKW32, PHC_CNKW32, PHB_GGKW32, ATT0_KW32, ATT2_KW32, ???) | MISSING VALUE FOR E0100R | N
0100 | CAMPBELL STADIUM | UC NODE ROOM, SPRINT | Y | E0100K | SUBMETER | 264 * Σ_KWH(P1,P2,P3) / Σ_sqft(414,459,576) | 264 * SUM(DINKW32, SCKB32, LANDIS_SPKW32) / 1449 | CALCULATION REQUIRES SUM OF KWH (E002A, E0020A, E0074A) AND GSF(SQ.FT.) FOR DIFFENBAUGH NODE, SCI. CENTER LIBRARY NODE, LANDIS NODE. SQFT FOR NODE ROOM AT STADIUM = 264. SQFT FOR DIFFENBAUGH NODE = 414, SCI. CENTER LIBRARY = 459, LANDIS NODE = 576. | N
0100 | CAMPBELL STADIUM | UC- TV HOOKUP, UCKW32 | Y | E0100J | SUBMETER | SET EQUAL TO | UCKW32 | NOT CONFIRMED YET | Y | E0100J_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UNIVERSITY CENTER EAST CONSESSIONS | Y | E0100L | SUBMETER | SET EQUAL TO | PHA_CNKW32 |  | Y | E0100L_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UNIVERSITY CENTER WEST CONSESSIONS | Y | E0100M | DIST/SUB | SET EQUAL TO | PHC_CNKW32 | THIS METER HAS BEEN RETIRED | N |  | Y
0100 | CAMPBELL STADIUM | UC "C" North Wireless AT&T3 | Y | E0100M1 | SUBMETER | SET EQUAL TO | ATT3KW32 | MONTH POINTS USE ATT3_KWXX format | Y | E0100M1_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC WEST CONSESSIONS UPSTREAM | Y | E0100M2 | VIRTUAL | SUBTRACT P1 - P2 | PHC_CNKW32 - ATT3_KW32 | I GUESS ALSO RETIRED SINCE THERE IS NO 0100M METER. | N
0100 | CAMPBELL STADIUM | UC GRAB & GO | Y | E0100N | SUBMETER | SET EQUAL TO | PHB_GGKW32 |  | Y | E0100N_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC "A" CenterGate Wireless AT&T0 | Y | E0100P | SUBMETER | SET EQUAL TO | ATT0KW32 | MONTH POINTS USE ATT0_KWXX format | Y | E0100P_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UC "A" North Wireless AT&T2 | Y | E0100Q | SUBMETER | SET EQUAL TO | ATT2KW32 | MONTH POINTS USE ATT2_KWXX format | Y | E0100Q_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | UNIVERSITY CENTER B FOOD TRUCK, TRES HAR. | Y | E0100R | SUBMETER | ??? | ??? | PHB_DEM_FT DEM IS USED
0113 | CARRAWAY BUILDING | CARRAWAY BLDG., CAKW32 | Y | E0113 | BUILDING | SET EQUAL TO | CAKW32 |  | Y | E0113_UTL_METER_DAY32 | Y
0113 | CARRAWAY BUILDING | CARRAWAY ARTIC CORE, CAKA32 | Y | E0113A | BUILDING | SET EQUAL TO | CAKA32 |  | Y | E0113A_UTL_METER_DAY32 | Y
0114 | ENGINEERING LAB BUILDING | ENGINEERING LAB WIND TUNNEL, ELKW32 | Y | E0114 | BUILDING | SET EQUAL TO | ENGLAB_KW32 |  | Y | E0114_UTL_METER_DAY32 | Y
0115 | HOWSER STADIUM | HOWSER BASEBALL STAD., | Y | E0115 | BUILDING | SET EQUAL TO | HOWKW32 |  | Y | E0115_UTL_METER_DAY32 | Y
0115 | HOWSER STADIUM | HOWSER SCOREBOARD | Y | E0115A | BUILDING | SET EQUAL TO | 0115_HSB_KW32 |  | Y | E0115A_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE BLDG., LVKW32 | Y | E0116 | BUILDING | SET EQUAL TO | LV_KW32 |  | Y | E0116_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE, WEATHER STATION, FL 1,2,3 NWKW32 | Y | E0116A | BUILDING | SET EQUAL TO | NWKW32 |  | Y | E0116A_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE, WEATHERSTATION, FL 4,5 NWKWA32 | Y | E0116B | BUILDING | SET EQUAL TO | NWKWA32 |  | Y | E0116B_UTL_METER_DAY32 | Y
0117 | HASKIN CIRCUS COMPLEX | CIRCUS HUT, CIRKW32 | Y | E0117 | BUILDING | SET EQUAL TO | CIRKW32 |  | Y | E0117_UTL_METER_DAY32 | Y
0121 | HARPE-JOHNSON BUILDING | ROTC BLDG., RTKW32 | Y | E0121 | BUILDING | SET EQUAL TO | 0121_KW32 |  | Y | E0121_UTL_METER_DAY32 | Y
0122 | TRACK PRESS BOX AND BLEACHERS | CELL TOWER VERIZON BY TRACK | Y | E0122_CELLTWR | BUILDING | SET EQUAL TO | 0122_VER_KW32 |  | Y | E0122_CELLTWR_UTL_METER_DAY32 | Y
0132 | TULLY GYM | TULLY GYM, TGKW32 | Y | E0132 | BUILDING | SET EQUAL TO | TGKW32 |  | Y | E0132_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STROZIER NORTH, SNKW32 | Y | E0134 | BUILDING | SET EQUAL TO | SNKW32 |  | Y | E0134_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STROZIER SOUTH, SSKW32 | N | E0134A | DIST | SET EQUAL TO | SSKW32 |  | Y | E0134A_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STROZIER COFFEE HOUSE, SS_SBKW32 | Y | E0134B | SUBMETER | SET EQUAL TO | SS_SBKW32 |  | Y | E0134B_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | UPSTREAM METER OF E0134A | Y | E0134C | VIRTUAL | SUBTRACT P1 - P2 -P3 | SSKW32, SNKW32, SS_SBKW32 |  | N
0135 | SANDELS BUILDING | SANDELS BLDG., SAKW32 | Y | E0135 | BUILDING | SET EQUAL TO | SA_KW32 |  | Y | E0135_UTL_METER_DAY32 | Y
0146 | KASHA LABORATORY | IMB, IMBKW32 | Y | E0146 | BUILDING | SET EQUAL TO | IMBKW32 |  | Y | E0146_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A SOUTH, M15-17E, UCKG32 | N | E0223A | DIST/SUB | SET EQUAL TO | 0200_M15-17E_KW32 |  | Y | E0223A_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC SIGN PRO AD NE | Y | E0223A1 | SUBMETER | SET EQUAL TO | ATH_PHA_S_KW32 |  | Y | E0223A1_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A SOUTH, M15-17E, UPSTREAM | Y | E0223A2 | VIRTUAL | SUBTRACT P1 - P2 | 0200_M15-117E_KW32, ATH_PHA_S_KW32 |  | N
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A NORTH, M15-17C, UCKH32 | N | E0223B | DIST/SUB | SET EQUAL TO | 0200_M15-17C_KW32 |  | Y | E0223B_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A SOUTH, WIRELESS AT&T1 CL1KW32 | Y | E0223B1 | SUBMETER | SET EQUAL TO | ATT1_KW32 | This specific point is not in desigo, but the points for every month (ex. ATT1_KW33-44) are in desigo. | Y | E0223B1_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A CELL TOWER, AT&T5_KW_32 | N | E0223B2 | SUBMETER | EMPTY | EMPTY | NOT NEEDED | N
0223 | UNIVERSITY CENTER - BUILDING A | UC "A" SKYBOX A/C DX UNITS | Y | E0223B5 | SUBMETER | SET EQUAL TO | SKYB_KW32 |  | Y | E0223B5_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC SIGN PRO AD SE | Y | E0223B4 | SUBMETER | SET EQUAL TO | ATH_PHA_N_KW32 |  | Y | E0223B4_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC "A" SOUTH CELL SERVICE VERIZON | Y | E0223B6 | SUBMETER | SET EQUAL TO | VERZ1KW32 |  | Y | E0223B6_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A UPSTREAM METER OF E0223B | Y | E0223B3 | VIRTUAL | SUBTRACT P1 - (P2 + P3 + P4 + P5) | 0200_M15-17C_KW32, ATT1_KW32, UCC_SKYBOX_KW32, ATH_PHA_N_KW32, CL1KW32 |  | N
0223 | UNIVERSITY CENTER - BUILDING A | UC PHASE A NORTH, M15-17D, UCKI32 | N | E0223C | SUBMETER | EMPTY | EMPTY | NOT NEEDED | N
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, ELEV & EMER CIR, UCKZ32 | Y | E0224A | SUBMETER | ??? | ??? | NOT FOUND - Meters are UCB_DEM_LS and UC_DEM_EQ
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, LEVELS 1-3, UCKP32 | N | E0224B | DIST/SUB | SET EQUAL TO | PHB13_KW32 |  | Y | E0224B_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B PUMPS, PHB_CW_HW | Y | E0224B1 | SUBMETER | SET EQUAL TO | 0224_PMP_KW32 |  | Y | E0224B1_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, LEVEL 3 SL3K32 | Y | E0224B2 | SUBMETER | SET EQUAL TO | SL3K32 |  | Y | E0224B2_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B LEVEL 2 KITCHEN, CLUB | Y | E0224B6 | SUBMETER | SET EQUAL TO | PHB_KITCH_KW32 |  | Y | E0224B6_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, LEVEL 1-3 UPSTREAM OF E0224B | Y | E0224B3 | VIRTUAL | SUBTRACT P1 - (P2+P3+P4) | UCKP32, PHB_CW_HW, SL3K32, PHB_KITCH_KW32 |  | N
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, LEVELS 4-7, UCKY32 | Y | E0224C | DIST/SUB | SET EQUAL TO | PHB47_KW32 |  | Y | E0224C_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, LEVEL4 SL4K32 | Y | E0224C1 | SUBMETER | SET EQUAL TO | SL4K32 |  | Y | E0224C1_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, SOUTH SCOREBOARD | Y | E0224C3 | SUBMETER | SET EQUAL TO | 0225_SB_KW32 |  | Y | E0224C3_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B LEVEL 5 KITCHEN 400AMP D1 E&G | Y | E0224C4 | SUBMETER | ??? | ??? | SLV5D3_KW32 IS A SUM OF C4 AND C5, BUT NOT SURE HOW THEY ARE SPLIT
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B LEVEL 5 KITCHEN 100 AMP D2 E&G | Y | E0224C5 | SUBMETER | ??? | ??? | SLV5D3_KW32 IS A SUM OF C4 AND C5, BUT NOT SURE HOW THEY ARE SPLIT
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B SIGN PRO AD SOUTH | Y | E0224C6 | SUBMETER | SET EQUAL TO | UCB_RIB_KW32 |  | Y | E0224C6_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UC PHASE B, LEVEL 4-7 UPSTREAM OF E0224C | Y | E0224C2 | VIRTUAL | SUBTRACT P1 - (P2+P3+P4+P5+P6) | PHB47_KW32, SL4K32,0225_SB_KW32, ??? , ??? , UCB_RIB_KW32 | MISSING VALUE FOR E0224C4 & E0224C5 | N
0224 | UNIVERSITY CENTER - BUILDING B | UCB TOWER EAST AND WEST COMBINED | Y | E0224D | SUBMETER | SET EQUAL TO | UCB_NEW_KW32 |  | Y | E0224D_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC PHASE C NORTH, FL 1-9, UCKR32 | N | E0225A | DIST/SUB | SET EQUAL TO | PHCN_KW32 |  | Y | E0225A_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC SIGN PRO AD NW | Y | E0225A1 | SUBMETER | SET EQUAL TO | ATH_PHC_N_KW32 |  | Y | E0225A1_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC PHASE C NORTH, FL 1-9, UCKR32 Upstream | Y | E0225A2 | VIRTUAL | SUBTRACT P1 - (P2+P3+P4) | PHCN_KW32, ATH_PHC_N_KW32, ATT4_KW32, UCC_SKYBOX_KW32 |  | N
0225 | UNIVERSITY CENTER - BUILDING C | UC "C" North Wireless AT&T4 | Y | E0225A3 | SUBMETER | SET EQUAL TO | ATT4KW32 | MONTHS HAVE FORMAT ATT4_KWXX | Y | E0225A3_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC "C" SKYBOX A/C DX UNITS | Y | E0225A4 | SUBMETER | SET EQUAL TO | UCC_SKYBOX_KW32 |  | Y | E0225A4_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC PHASE C SOUTH, FL 1-6 UCKQ32 | Y | E0225B | DIST/SUB | SET EQUAL TO | PHCS_KW32 |  | Y | E0225B_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC SIGN PRO AD SW | Y | E0225B1 | SUBMETER | SET EQUAL TO | ATH_PHC_S_KW32 |  | Y | E0225B1_UTL_METER_DAY32 | Y
0225 | UNIVERSITY CENTER - BUILDING C | UC PHASE C SOUTH, FL 1-6 UCKQ32 -Upstream | Y | E0225B2 | VIRTUAL | SUBTRACT P1 - P2 | PHCS_KW32, ATH_PHC_S_KW32 |  | N
0226 | UNIVERSITY CENTER - BUILDING D | UC PHASE D, COMM BLDG, CMKW32 | N | E0226 | DIST/SUB | SET EQUAL TO | CMKW32 |  | Y | E0226_UTL_METER_DAY32 | Y
0226 | UNIVERSITY CENTER - BUILDING D | UC PHASE D, NORTH END SCOREBOARD, UCKL32 | Y | E0226A | SUBMETER | SET EQUAL TO | UCKL32 | VALUE IS OFF | Y | E0226A_UTL_METER_DAY32 | Y
0226 | UNIVERSITY CENTER - BUILDING D | UC PHASE D, NORTH END SKY BOXES, UCKV32 | Y | E0226B | SUBMETER | SET EQUAL TO | SKYBX_KW32 |  | Y | E0226B_UTL_METER_DAY32 | Y
0226 | UNIVERSITY CENTER - BUILDING D | UC PHASE D, COM FOOD SVC | Y | E0226C | SUBMETER | SET EQUAL TO | CM_KITCHEN_KW32 |  | Y | E0226C_UTL_METER_DAY32 | Y
0226 | UNIVERSITY CENTER - BUILDING D | UC PHASE D, E0226 UPSTREAM METER | Y | E0226D | VIRTUAL | SUBTRACT P1 - (P2+P3+P4) | CMKW32, UCKL32, SKYBX_KW32, CM_KITCHEN_KW32 |  | N
0240 | MARCHING CHIEFS TOWER & FIELD | MARCHING CHIEF BAND FIELD | Y | E0240 | BUILDING | SET EQUAL TO | BND_KW32 |  | Y | E0240_UTL_METER_DAY32 | Y
0260 | ASKEW STUDENT LIFE CENTER | STUDENT LIFE BLDG., LIKW32 | Y | E0260 | BUILDING | SET EQUAL TO | LIKW32 |  | Y | E0260_UTL_METER_DAY32 | Y
0293 | HAZARDOUS WASTE FACILITY | HAZARDOUS WASTE BLDG., HWKW32 | Y | E0293 | BUILDING | SET EQUAL TO | 0293_KW32 |  | Y | E0293_UTL_METER_DAY32 | Y
0378 | PARKING GARAGE #2 - TRADITIONS WAY | PARKING GARAGE #2, | Y | E0378 | BUILDING | SET EQUAL TO | PG2KW32 |  | Y | E0378_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR BLDG | N | E0379 | DIST | SET EQUAL TO | SVB_KW32 | VALUE IS OFF | Y | E0379_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, E&G 1ST FLOOR, SVH1_KW32 | Y | E0379A | SUBMETER | SET EQUAL TO | SVH1_KW32 |  | Y | E0379A_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, 24 HOUR DINER, SVH1A_KW32 | Y | E0379B | SUBMETER | SET EQUAL TO | SVH1A_KW32 |  | Y | E0379B_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, UNION 2ND FLOOR, SVH2_KW32 | Y | E0379C | SUBMETER | SET EQUAL TO | SVH2_KW32 |  | Y | E0379C_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, E&G 3RD FLOOR, SVH3_KW32 | Y | E0379D | SUBMETER | SET EQUAL TO | SVH3_KW32 |  | Y | E0379D_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, UPSTREAM | Y | E0379E | VIRTUAL | SUBTRACT P1 - (P2 + P3 + P4 + P5) | SVB_KW32, SVH1_KW32, SVH1A_KW32, SVH2_KW32, SVH3_KW32 |  | N
0385 | STILES-SMITH TEAM BUILDING | WOMENS SOCCER / SOFTBALL, WSKW32 | Y | E0385 | BUILDING | SET EQUAL TO | WSKW32 |  | Y | E0385_UTL_METER_DAY32 | Y
0488 | SEMINOLE CAFE RESTURANT | WEST DINING HALL, WDINING_KW32 | Y | E0488 | BUILDING | SET EQUAL TO | WDINING_KW32 |  | Y | E0488_UTL_METER_DAY32 | Y
0495 | RAGANS HALL 1 (A) | NEW RESIDENCE HALL 1, REA_KW32 | Y | E0495 | BUILDING | SET EQUAL TO | 0495_RAGANS_EM32 |  | Y | E0495_UTL_METER_DAY32 | Y
0496 | RAGANS HALL 2 (B) | NEW RESIDENCE HALL 2, REB_KW32 | Y | E0496 | BUILDING | SET EQUAL TO | 0496_RAGANS_EM32 |  | Y | E0496_UTL_METER_DAY32 | Y
0497 | RAGANS HALL 3 (C) | NEW RESIDENCE HALL 3, REC_KW32 | Y | E0497 | BUILDING | SET EQUAL TO | 0497_RAGANS_EM32 |  | Y | E0497_UTL_METER_DAY32 | Y
0498 | RAGANS HALL 4 (D) | NEW RESIDENCE HALL 4, RED_KW32 | Y | E0498 | BUILDING | SET EQUAL TO | 0498_RAGANS_EM32 |  | Y | E0498_UTL_METER_DAY32 | Y
0904 |  | SALLEY HALL TENNIS CT. MANUAL READ | Y | E0904 | BUILDING | SET EQUAL TO | MANUAL READ |  | N
0904 |  | PARKING LOT LIGHTS, WEST OF TENNIS CT. | Y | E0904A | BUILDING | SET EQUAL TO | MANUAL READ |  | N
4001 | COLLEGE OF MEDICINE - THRASHER BUILDING | MED SCHOOL, ADMIN | Y | E4001 | BUILDING | SET EQUAL TO | MED_SCHA_KW32 |  | Y | E4001_UTL_METER_DAY32 | Y
4002 | COLLEGE OF MEDICINE - RESEARCH BUILDING | MED SCHOOL, RESEARCH | Y | E4002 | BUILDING | SET EQUAL TO | MED_SCHB_KW32 |  | Y | E4002_UTL_METER_DAY32 | Y
4004 | PSYCHOLOGY DEPARTMENT BUILDING | NEW PSY BLDG.& AUD & CONSTRUCTION | Y | E4004 | BUILDING | SET EQUAL TO | PSYR_KW32 |  | Y | E4004_UTL_METER_DAY32 | Y
4006 | PARKING GARAGE #3 - SPIRIT WAY | PARKING GARAGE #3, | Y | E4006 | BUILDING | SET EQUAL TO | PG3KW32 |  | Y | E4006_UTL_METER_DAY32 | Y
4007 | KING LIFE SCIENCE BUILDING | LIFE SCIENCE, METER "A" | Y | E4007 | BUILDING | SET EQUAL TO | LIFE_A_KW32 |  | Y | E4007_UTL_METER_DAY32 | Y
4007 | KING LIFE SCIENCE BUILDING | LIFE SCIENCE, METER "B" | Y | E4007B | BUILDING | SET EQUAL TO | LIFE_B_KW32 |  | Y | E4007B_UTL_METER_DAY32 | Y
4008 | CHEMICAL SCIENCE LABORATORIES | New Chemistry Bldg, METER "A" | Y | E4008 | BUILDING | SET EQUAL TO | CHEM_DEM02_KW32 |  | Y | E4008_UTL_METER_DAY32 | Y
4008 | CHEMICAL SCIENCE LABORATORIES | New Chemistry Bldg, METER "B" | Y | E4008B | BUILDING | SET EQUAL TO | CHEM_DEM03_KW32 |  | Y | E4008B_UTL_METER_DAY32 | Y
4009 | CLASSROOM BUILDING (HCB) | CLASSROOM BLDG. | Y | E4009 | BUILDING | SET EQUAL TO | CLASS_KW32 |  | Y | E4009_UTL_METER_DAY32 | Y
4010 | EOAS BUILDING | EAOS Building Meter | Y | E4010 | BUILDING | SET EQUAL TO | 4010_KW32 |  | Y | E4010_UTL_METER_DAY32 | Y
4011 | DUNLAP SUCCESS CENTER | Student Success Building | Y | E4011 | BUILDING | SET EQUAL TO | STSC_KW32 | DOES NOT LET ME CREATE NOR DELETE TREND | Y | E4011_UTL_METER_DAY32 | Y
4014 | PARKING GARAGE #4 - CALL ST | Parking Garage #4 | Y | E4014 | BUILDING | SET EQUAL TO | PG4_KW32 |  | Y | E4014_UTL_METER_DAY32 | Y
4018 | NEW STUDENT UNION | New Union entire complex | Y | E4018 | BUILDING | SET EQUAL TO | 4018_SU_KW32 |  | Y | E4018_UTL_METER_DAY32 | Y
4020 | WILDWOOD HALLS 1 | New Residents Hall # 5, Wildwood dr. South | Y | E4020 | BUILDING | SET EQUAL TO | WILD_S_KW32 |  | Y | E4020_UTL_METER_DAY32 | Y
4021 | WILDWOOD HALLS 2 | New Residents Hall # 6, Wildwood dr. North | Y | E4021 | BUILDING | SET EQUAL TO | WILD_N_KW32 |  | Y | E4021_UTL_METER_DAY32 | Y
4022 | TRADITIONS HALL | TRADITIONS HALL | Y | E4022 | BUILDING | SET EQUAL TO | WILD_3_KW32 |  | Y | E4022_UTL_METER_DAY32 | Y
4025 | PARKING GARAGE #5 - ST AUGUSTINE ST | PARKING GARAGE #5 | Y | E4025 | BUILDING | SET EQUAL TO | PG5_KW32 |  | Y | E4025_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | JOHNSTON ANNEX, BUILDING METER | N | E4029 | DIST | SET EQUAL TO | JBA_KW32 |  | Y | E4029_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | JOHNSTON ANNEX, CHICK-FIL-A | Y | E4029A | SUBMETER | SET EQUAL TO | JBA_CFKW32 | VALUE OFF | Y | E4029A_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | JOHNSTON ANNEX, RISING ROLL | Y | E4029B | SUBMETER | SET EQUAL TO | JBA_RRKW32 | VALUE OFF | Y | E4029B_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | JOHNSTON ANNEX, POD | Y | E4029C | SUBMETER | SET EQUAL TO | JBA_PODKW32 | VALUE OFF | Y | E4029C_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | JOHNSTON ANNEX, UPSTREAM ,E&G usage | Y | E4029D | VIRTUAL | SUBTRACT P1 - (P2+P3+P4) | JBA_KW32, JBA_CFKW32, JBA_RRKW32, JBA_PODKW32 |  | N
4030 | COBURN WELLNESS CENTER | WELLNESS CENTER | N | E4030 | DIST | SET EQUAL TO | WEL_TOT_KW32 |  | Y | E4030_UTL_METER_DAY32 | Y
4030 | COBURN WELLNESS CENTER | WELLNESS CENTER, HEALTH | Y | E4030A | SUBMETER | MULTIPLY P1*0.67 | (WEL_TOT_KW32)*0.67 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS CENTER, FITNESS | Y | E4030B | SUBMETER | MULTIPLY P1*0.10 | (WEL_TOT_KW32)*0.10 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS CENTER, NURSING | Y | E4030C | SUBMETER | MULTIPLY P1*0.23 | (WEL_TOT_KW32)*0.23 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS CENTER, UPSTREAM | N | E4030D | VIRTUAL | SUBTRACT P1 - (P2+P3+P4) | WEL_TOT_KW32, (WEL_TOT_KW32)*0.67, (WEL_TOT_KW32)*0.10, (WEL_TOT_KW32)*0.23 | SHOULD EQUAL 0 | N
4031 | THE GLOBE | Student Success Building, Phase 2 | Y | E4031 | BUILDING | SET EQUAL TO | STC2_KW32 |  | Y | E4031_UTL_METER_DAY32 | Y
4060 | DORMAN HALL | Residents Hall # 10, Dorman Hall | Y | E4060 | BUILDING | SET EQUAL TO | 4060_KW32 |  | Y | E4060_UTL_METER_DAY32 | Y
4061 | DEVINEY HALL | Residents Hall # 11, Deviney Hall | Y | E4061 | BUILDING | SET EQUAL TO | 4061_KW32 |  | Y | E4061_UTL_METER_DAY32 | Y
4062 | AZALEA HALL | Residents Hall, Azalea Hall | Y | E4062 | BUILDING | SET EQUAL TO | 4062_KW32 |  | Y | E4062_UTL_METER_DAY32 | Y
4062 | AZALEA HALL | Azalea Hall Food Service | Y | E4062A | BUILDING | SET EQUAL TO | 4062_FS_KW32 |  | Y | E4062A_UTL_METER_DAY32 | Y
4063 | MAGNOLIA HALL | Residents Hall, Magnolia Hall | Y | E4063 | BUILDING | SET EQUAL TO | 4063_KW32 |  | Y | E4063_UTL_METER_DAY32 | Y
4090 | DUNLAP PRACTICE FACILITY | Indoor Practice Facility | Y | E4090 | BUILDING | SET EQUAL TO | IFPF_KW32 |  | Y | E4090_UTL_METER_DAY32 | Y
0030 | CENTRAL UTILITIES PLANT | CUP CHILLERS SUBSTATION, M15CUPKW32 | N | EP0030 | BUILDING | SET EQUAL TO | M157KWH32 | VALUE OFF | Y | EP0030_UTL_METER_DAY32 | Y
0030 | CENTRAL UTILITIES PLANT | CUP- BOILERS, CPKA32 | N | EP0030A | BUILDING | SET EQUAL TO | CUP_KW32 | VALUE OFF | Y | EP0030A_UTL_METER_DAY32 | Y
0033 | SATELLITE UTILITIES PLANT 1 | SATELLITE PLANT, SUBST METER, M1515KW32 | N | EP0033 | BUILDING | SET EQUAL TO | SAT1_TOT_KW32 |  | Y | EP0033_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | PLANT 3, STADIUM M15-16C UCKE32 | N | EP0100A | SUBMETER | SET EQUAL TO | 0200_M15-23C_KW32 |  | Y | EP0100A_UTL_METER_DAY32 | Y
4013 | SATELLITE UTILITIES PLANT 2 | Satellite Plant #2 | N | EP4013 | BUILDING | SET EQUAL TO | SAT2_TOT_KW32 |  | Y | EP4013_UTL_METER_DAY32 | Y
0100 | CAMPBELL STADIUM | WELL PUMPS FOR STAD CHILLERS, ACPMPKW32 | N | EPU001 | BUILDING | SET EQUAL TO | ACPMPKW32 |  | Y | EPU001_UTL_METER_DAY32 | Y
Total |  | 213 | [5 empty] | 30 |  | 213 | 178
ALL OF THE ALIAS ARE IN DESIGO
0224_FOOD_TRUCK_TOTAL_KWH
Note on K87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Alias manually input. This meter consists of TWO BAS points. They are both aliased and differentiated by using .1 and .2 at the end of the alias.
Note on E115: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: meterID: E0122-CELLTWR. Replaced - with _ for the alias formula.
Note on H127: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ppcl shows 4 points used to obtain the month values: "AT&T1:CONSUMPTN HI" - "ATT1_KWH_MH" + ("AT&T1:CONSUMPTN LO" - "ATT1_KWH_ML"). points "MH" and "ML" are in Desigo, but the other two are not. They are also not trended so I can't see their value historically.
Note on D213: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All highlighted are production meters. They are not billed.

## STEAM
UTILITIES BILLING
STEAM
BLDG # | BLDG NAME | CUSTOMER | BILLED IN AIM (Y/N) | METER ID | METER TYPE | CALC | BAS POINT NAME(S) | NOTES | NEED ALIAS? (Y/N) | ALIAS | ALIAS IN DESIGO? (Y/N)
0000 |  | CUP MASTER STEAM METER | N | ST0000 | MASTER | SET EQUAL TO | B4ST32 |  | Y | ST0000_UTL_METER_DAY32 | Y
0001 | WESTCOTT BUILDING | WESTCOTT. WEST32 | Y | ST0001 | BUILDING | SET EQUAL TO | WE_ST32 |  | Y | ST0001_UTL_METER_DAY32 | Y
0002 | DIFFENBAUGH BUILDING | DIFFENBAUGH, DIST32 | Y | ST0002 | BUILDING | SET EQUAL TO | DIST32 |  | Y | ST0002_UTL_METER_DAY32 | Y
0003 | WILLIAMS BUILDING | WILLIAMS BLDG., WIST32 | Y | ST0003 | BUILDING | SET EQUAL TO | WIST32 |  | Y | ST0003_UTL_METER_DAY32 | Y
0004 | DODD HALL | DODD HALL , DHST32 | Y | ST0004 | BUILDING | SET EQUAL TO | DH_ST32 |  | Y | ST0004_UTL_METER_DAY32 | Y
0005 | CRIMINOLOGY AND CRIMINAL JUSTICE BUILDING | PSYCHOLOGY ,POST32 | Y | ST0005 | BUILDING | SET EQUAL TO | EPS_ST32 |  | Y | ST0005_UTL_METER_DAY32 | Y
0006 | KELLOGG BUILDING | KELLOGG RESEARCH , PRST32 | Y | ST0006 | BUILDING | SET EQUAL TO | PRST32 |  | Y | ST0006_UTL_METER_DAY32 | Y
0007 | FINE ARTS BUILDING | FINE ARTS ,FAST32 | Y | ST0007 | BUILDING | SET EQUAL TO | FA_ST32 |  | Y | ST0007_UTL_METER_DAY32 | Y
0008 | BELLAMY BUILDING | BELLAMY , BEST32 | Y | ST0008 | BUILDING | SET EQUAL TO | BESTN32 |  | Y | ST0008_UTL_METER_DAY32 | Y
0009 | BIOMEDICAL RESEARCH FACILITY | BIO MED RESEARCH , BMST32 | Y | ST0009 | BUILDING | SET EQUAL TO | 0009_ST_32 |  | Y | ST0009_UTL_METER_DAY32 | Y
0012 | JENNIE MURPHREE HALL | JENNIE MURPHREE HALL , JMST32 | Y | ST0012 | BUILDING | SET EQUAL TO | 0012_ST32 |  | Y | ST0012_UTL_METER_DAY32 | Y
0013 | REYNOLDS HALL | REYNOLDS HALL , REST32 | Y | ST0013 | BUILDING | SET EQUAL TO | 0013_ST32 |  | Y | ST0013_UTL_METER_DAY32 | Y
0014 | BRYAN HALL | BRYAN HALL , BHST32 | Y | ST0014 | BUILDING | SET EQUAL TO | 0014_STMT32 |  | Y | ST0014_UTL_METER_DAY32 | Y
0015 | BROWARD HALL | BROWARD HALL , BRST32 | Y | ST0015 | BUILDING | SET EQUAL TO | BRST32 |  | Y | ST0015_UTL_METER_DAY32 | Y
0016 | GILCHRIST HALL | GILCHRIST HALL , GHST32 | Y | ST0016 | BUILDING | SET EQUAL TO | GHST32 |  | Y | ST0016_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON DINING , JO_EG_ST32 | Y | ST0017A | SUBMETER | SET EQUAL TO | N/A | MANUALLY CALCULATED BY NARIMAN. | N
0017 | JOHNSTON BUILDING | JOHNSTON DINING , JO_ST32 | N | ST0017B | DISTRIBUTION | ADD P1 + P2 | JO_ST32, N/A
0017 | JOHNSTON BUILDING | UPSTREAM METER FOR SWANNEE FOOD SVS | Y | ST0017C | VIRTUAL | SET EQUAL TO | JO_ST32 |  | Y | ST0017C_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON NEW MIDDLE SECTION | Y | ST0017D | BUILDING | SET EQUAL TO | JB_ST32 |  | Y | ST0017D_UTL_METER_DAY32 | Y
0019 | SHORES BUILDING | LIBRARY SCIENCE , LSST32 | Y | ST0019 | BUILDING | SET EQUAL TO | LS_ST32 |  | Y | ST0019_UTL_METER_DAY32 | Y
0020 | DIRAC SCIENCE LIBRARY | DIRAC SCIENCE LIBRARY , SCST32 | Y | ST0020 | BUILDING | SET EQUAL TO | SCST32 |  | Y | ST0020_UTL_METER_DAY32 | Y
0025 | MONTGOMERY | MONTGOMERY GYM , MGST32 | Y | ST0025 | BUILDING | SET EQUAL TO | MGST32 |  | Y | ST0025_UTL_METER_DAY32 | Y
0026 | LEACH CENTER | NATATORIUM , NAST32 | Y | ST0026 | BUILDING | ADD P1+ P2 + P3 | NAST32, NADS32, NAPS32 | THE TOTAL FOR ALL THESE POINTS IS NASTT32 BUT THE POINT ONLY EXIST FOR 33 TO 44 | Y | ST0026_UTL_METER_DAY32 | Y
0028 | THAGARD BUILDING | THAGARD HEALTH CTR, HCST32 | Y | ST0028 | BUILDING | SET EQUAL TO | HCST32 |  | Y | ST0028_UTL_METER_DAY32 | Y
0035 | HOFFMAN TEACHING LAB | CHEMISTRY II , HOST32 | Y | ST0035 | BUILDING | SET EQUAL TO | HOST32 |  | Y | ST0035_UTL_METER_DAY32 | Y
0036 | ROGERS BUILDING (OSB) | OCEANOGRAPHY STATISTICS , OSST32 | Y | ST0036 | BUILDING | SET EQUAL TO | OSST32 |  | Y | ST0036_UTL_METER_DAY32 | Y
0037 | FISHER LECTURE HALL | FISHER LECTURE HALL | Y | ST0037 | BUILDING | SET EQUAL TO | FLST32 |  | Y | ST0037_UTL_METER_DAY32 | Y
0038 | DITTMER CHEMISTRY LAB | CHEMISTRY I , DTST32 | Y | ST0038 | BUILDING | SET EQUAL TO | DTST32 |  | Y | ST0038_UTL_METER_DAY32 | Y
0039 | BIOLOGY UNIT I | BIOLOGY , BIST32 | Y | ST0039 | BUILDING | SET EQUAL TO | 0039_ST32 |  | Y | ST0039_UTL_METER_DAY32 | Y
0040 | DUXBURY HALL | SCHOOL OF NURSING , NRST32 | Y | ST0040 | BUILDING | SET EQUAL TO | 0040_ST32 |  | Y | ST0040_UTL_METER_DAY32 | Y
0041 | KEEN BUILDING | KEEN , KEST32 | Y | ST0041 | BUILDING | SET EQUAL TO | KEST32 |  | Y | ST0041_UTL_METER_DAY32 | Y
0042 | COLLINS RESEARCH BUILDING | NUCLEAR RESEARCH, NUST32 | Y | ST0042 | BUILDING | SET EQUAL TO | NUST32 |  | Y | ST0042_UTL_METER_DAY32 | Y
0044 | ROGERS HALL | ROGERS HALL, ROST32 | Y | ST0044 | BUILDING | SET EQUAL TO | RO_ST32 |  | Y | ST0044_UTL_METER_DAY32 | Y
0045 | RICHARDS BUILDING | UNDERGRAD LAB RICHARDS, RIST32 | Y | ST0045 | BUILDING | SET EQUAL TO | 0045_ST32 |  | Y | ST0045_UTL_METER_DAY32 | Y
0046 | SALLEY HALL | SALLEY HALL, SLST32 | Y | ST0046 | BUILDING | SET EQUAL TO | SH_ST32 |  | Y | ST0046_UTL_METER_DAY32 | Y
0050 | STONE BUILDING | STONE, STST32 | Y | ST0050 | BUILDING | SET EQUAL TO | STN_ST32 |  | Y | ST0050_UTL_METER_DAY32 | Y
0052 | ROVETTA BUILDING B | BUSINESS, BWST32 | Y | ST0052 | BUILDING | SET EQUAL TO | ROV_B_ST32 |  | Y | ST0052_UTL_METER_DAY32 | Y
0054 | HOUSEWRIGHT MUSIC BUILDING | NEW MUSIC HOUSEWRIGHT, NMST32 | Y | ST0054 | BUILDING | SET EQUAL TO | 0054_ST32 |  | Y | ST0054_UTL_METER_DAY32 | Y
0055 | CAROTHERS HALL | EDUCATION CAROTHERS, EDST32 | Y | ST0055 | BUILDING | SET EQUAL TO | ED_ST32 |  | Y | ST0055_UTL_METER_DAY32 | Y
0057 | PEPPER BUILDING | CLAUDE PEPPER, PBST32 | Y | ST0057 | BUILDING | SET EQUAL TO | PBST32 |  | Y | ST0057_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARKING GARAGE #1, PGST32 | N | ST0070 | DISTRIBUTION | SET EQUAL TO | PGST32 |  | Y | ST0070_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARKING GARAGE #1 | Y | ST0070A | SUBMETER | SET EQUAL TO | N/A | MANUALLY CALCULATED BY NARIMAN. | N |  | N
0070 | PARKING GARAGE #1 - WOODWARD AVE | UPSTREAM METER, PARKING GARAGE #1 | Y | ST0070B | VIRTUAL | SUBSTRACT P1 - P2 | PGST32, N/A
0072 | LONGMIRE BUILDING | LONGMIRE, LOST32 | Y | ST0072 | BUILDING | SET EQUAL TO | LOST32 |  | Y | ST0072_UTL_METER_DAY32 | Y
0074 | LANDIS HALL | LANDIS HALL, LHST32 | Y | ST0074 | BUILDING | SET EQUAL TO | LANDIS_ST32 |  | Y | ST0074_UTL_METER_DAY32 | Y
0075 | MCCOLLUM HALL | MCCOLLUM HALL, MCST32 | Y | ST0075 | BUILDING | SET EQUAL TO | MH_ST32 |  | Y | ST0075_UTL_METER_DAY32 | Y
0076 | TANNER HALL | 840 W JEFF PUBLIC SFTY, PSST32 | Y | ST0076 | BUILDING | SET EQUAL TO | PSST32 |  | Y | ST0076_UTL_METER_DAY32 | Y
0077 | MENDENHALL BUILDING A | MENDENHALL MAINT BLDG A, MAST32 | Y | ST0077 | BUILDING | SET EQUAL TO | MAST32 |  | Y | ST0077_UTL_METER_DAY32 | Y
0085 | CAWTHON HALL | CAWTHON HALL, CAWST32 | Y | ST0085 | BUILDING | SET EQUAL TO | CAWST32 |  | Y | ST0085_UTL_METER_DAY32 | Y
0089 | KUERSTEINER MUSIC BUILDING | MUSIC, MSST32 | Y | ST0089 | BUILDING | SET EQUAL TO | MS_ST32 |  | Y | ST0089_UTL_METER_DAY32 | Y
0091 | MCINTOSH TRACK & FIELD BUILDING | TRACK, HPL | Y | ST0091 | BUILDING | SET EQUAL TO | HPL_ST32 |  | Y | ST0091_UTL_METER_DAY32 | Y
0113 | CARRAWAY BUILDING | CARRAWAY, CAST32 | Y | ST0113 | BUILDING | SET EQUAL TO | CAST32 |  | Y | ST0113_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE, LVST32 | Y | ST0116 | BUILDING | SET EQUAL TO | LV_ST32 |  | Y | ST0116_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | WEATHER STATION ALL FL, NW1-5ST32 | N | ST0116A | DISTRIBUTION | SET EQUAL TO | NWST32
0116 | LOVE BUILDING | NOAA AT LOVE BLDG , NWST32 | Y | ST0116B | SUBMETER | MULTIPLY P1*0.35 | NWST32 |  | Y | ST0116B_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | UPSTREAM WEATHER STATION, E&G | Y | ST0116C | VIRTUAL | MULTIPLY P1*0.65 | NWST32
0121 | HARPE-JOHNSON BUILDING | ROTC, RTST32 | Y | ST0121 | BUILDING | ??? | ??? | THE POINT FOR THIS METER EXISTS HOWEVER IT DOES NOT HAVE A VALUE IN INSIGHT. ANOTHER POINT WAS FOUND FOR THIS BUILDING 0121_ST32 BUT THE UNITS ARE IN LBS AND THE VALUE IS NOT EXACT (THE UNIT IN INSIGHT FOR THIS POINT IS IN LBS INSTEAD OF LBM) | Y | ST0121_UTL_METER_DAY32 | N
0132 | TULLY GYM | TULLY GYM, TGST32 | Y | ST0132 | BUILDING | SET EQUAL TO | TGST32 |  | Y | ST0132_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STROZIER LIBRARY, SNST32 | Y | ST0134 | BUILDING | SET EQUAL TO | SNST32 |  | Y | ST0134_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STROZIER LIBRARY, SSST32 | Y | ST0134A | BUILDING | SET EQUAL TO | SSST32 |  | Y | ST0134A_UTL_METER_DAY32 | Y
0135 | SANDELS BUILDING | SANDELS, SAST32 | Y | ST0135 | BUILDING | SET EQUAL TO | SAST32 |  | Y | ST0135_UTL_METER_DAY32 | Y
0146 | KASHA LABORATORY | IMB, IMBST32 | Y | ST0146 | BUILDING | SET EQUAL TO | IMBST32 |  | Y | ST0146_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UCC COMPLEX | N | ST0223 | DISTRIBUTION | SET EQUAL TO | APST32 |  | Y | ST0223_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UPSTREAM METER FOR UUC | Y | ST0223A | VIRTUAL | SUBSTRACT P1 - (P2 + P3 + P4) | APST32, 0224_CLUB_ST32, 0224_ATHLETICS_ST32, COMST32 |  | N
0224 | UNIVERSITY CENTER - BUILDING B | UNIV CLUB CORP S. END ZONE, SBOS32 | Y | ST0224 | SUBMETER | SET EQUAL TO | 0224_CLUB_ST32 |  | Y | ST0224_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UCB TOWERS EAST & WEST | Y | ST0224TWS | SUBMETER | SET EQUAL TO | 0224_ATHLETICS_ST32 |  | Y | ST0224TWS_UTL_METER_DAY32 | Y
0226 | UNIVERSITY CENTER - BUILDING D | COMM BLDG, TOTAL, COMST32 | Y | ST0226 | SUBMETER | SET EQUAL TO | COMST32 |  | Y | ST0226_UTL_METER_DAY32 | Y
0260 | ASKEW STUDENT LIFE CENTER | STUDENT LIFE, LIST32 | Y | ST0260 | BUILDING | SET EQUAL TO | LIST32 |  | Y | ST0260_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SERVICES, SV_ST | N | ST0379 | DISTRIBUTION | ADD P1 + P2 + P3 + P4 | SV100_ST32, SV200_ST32, SV300_ST32, SV_DOM_ST32 |  | N
0379 | STUDENT SERVICES BUILDING | STUDENT SVS, 1ST FL, SV_LVL_STEAM_32 | Y | ST0379A | SUBMETER | SET EQUAL TO | SV100_ST32 |  | Y | ST0379A_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVS, 3RD FL, SV_LVL3_STEAM_32 | Y | ST0379B | SUBMETER | SET EQUAL TO | SV300_ST32 |  | Y | ST0379B_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVS, 2ND FL, SV_LVL2_STEAM_32 | Y | ST0379C | SUBMETER | SET EQUAL TO | SV200_ST32 |  | Y | ST0379C_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVS, DINER, SV_LVL1A_STEAM_32 | Y | ST0379D | SUBMETER | SET EQUAL TO | SV_DOM_ST32 |  | Y | ST0379D_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | UPSTREAM METER FOR BUILDING 0379 | N | ST0379E | VIRTUAL | SUBTRACT P1 - (P2 + P3 + P4 + P5) | (SV100_ST32, SV200_ST32, SV300_ST32, SV_DOM_ST32), SV100_ST32, SV200_ST32, SV300_ST32, SV_DOM_ST32 |  | N
0488 | SEMINOLE CAFE RESTURANT | WEST CAMPUS DINING, WDINING_ST32 | Y | ST0488 | BUILDING | SET EQUAL TO | WDINING_ST32 |  | Y | ST0488_UTL_METER_DAY32 | Y
0495 | RAGANS HALL 1 (A) | NEW RESIDENCE HALL B.DG A, REAST32 | Y | ST0495 | BUILDING | SET EQUAL TO | REAST32 |  | Y | ST0495_UTL_METER_DAY32 | Y
0496 | RAGANS HALL 2 (B) | NEW RESIDENCE HALL, BLDG B, REBST32 | Y | ST0496 | BUILDING | SET EQUAL TO | REBST32 |  | Y | ST0496_UTL_METER_DAY32 | Y
0497 | RAGANS HALL 3 (C) | NEW RESIDENCE HALL BLDG C, RECST32 | Y | ST0497 | BUILDING | SET EQUAL TO | RECST32 |  | Y | ST0497_UTL_METER_DAY32 | Y
0498 | RAGANS HALL 4 (D) | NEW RESIDENCE HALL BLDG D, REDST32 | Y | ST0498 | BUILDING | SET EQUAL TO | REDST32 |  | Y | ST0498_UTL_METER_DAY32 | Y
4001 | COLLEGE OF MEDICINE - THRASHER BUILDING | MEDICAL SCHOOL, MED_SCH_ST32 | Y | ST4001 | BUILDING | SET EQUAL TO | MED_SCH_ST32 |  | Y | ST4001_UTL_METER_DAY32 | Y
4004 | PSYCHOLOGY DEPARTMENT BUILDING | PSY BLDG. | Y | ST4004 | BUILDING | SET EQUAL TO | PSY_ST32 |  | Y | ST4004_UTL_METER_DAY32 | Y
4007 | KING LIFE SCIENCE BUILDING | LIFE SCIENCES | Y | ST4007 | BUILDING | SET EQUAL TO | LIFE_ST32 |  | Y | ST4007_UTL_METER_DAY32 | Y
4008 | CHEMICAL SCIENCE LABORATORIES | NEW CHEMISTRY | Y | ST4008 | BUILDING | SET EQUAL TO | CHEM_ST32 |  | Y | ST4008_UTL_METER_DAY32 | Y
4009 | CLASSROOM BUILDING (HCB) | CLASSROOM BLDG | Y | ST4009 | BUILDING | SET EQUAL TO | CLASS_ST32 |  | Y | ST4009_UTL_METER_DAY32 | Y
4011 | DUNLAP SUCCESS CENTER | Student Success Building | Y | ST4011 | BUILDING | SET EQUAL TO | STSC_ST32 |  | Y | ST4011_UTL_METER_DAY32 | Y
4020 | WILDWOOD HALLS 1 | New Residents Hall # 5, Wildwood dr. South | Y | ST4020 | BUILDING | SET EQUAL TO | WILD_S_ST32 |  | Y | ST4020_UTL_METER_DAY32 | Y
4021 | WILDWOOD HALLS 2 | New Residents Hall # 6, Wildwood dr. North | Y | ST4021 | BUILDING | SET EQUAL TO | WILD_N_ST32 |  | Y | ST4021_UTL_METER_DAY32 | Y
4022 | TRADITIONS HALL | TRADITIONS HALL | Y | ST4022 | BUILDING | SET EQUAL TO | WILD_3_ST32 |  | Y | ST4022_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, total usage | N | ST4029 | DISTRIBUTION | SET EQUAL TO | JBA_ST32 |  | Y | ST4029_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, Chick-fil-a | Y | ST4029A | SUBMETER | P1*0.12 | JBA_ST32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, Rising Roll | Y | ST4029B | SUBMETER | P1*0.11 | JBA_ST32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, POD | Y | ST4029C | SUBMETER | P1*0.11 | JBA_ST32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, E&G | Y | ST4029D | SUBMETER | P1*0.66 | JBA_ST32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, Remainder | N | ST4029E | VIRTUAL | SUBTRACT P1 - (P2 + P3 + P4 +P5) | JBA_ST32, JBA_ST32*0.12, JBA_ST32*0.11, JBA_ST32*0.11, JBA_ST32*0.66 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | Wellness Center | N | ST4030 | DISTRIBUTION | SET EQUAL TO | WEL_ST32 |  | Y | ST4030_UTL_METER_DAY32 | Y
4030 | COBURN WELLNESS CENTER | WELLNESS, HEALTH | Y | ST4030A | SUBMETER | MULTIPLY P1*0.67 | (WEL_ST32)*0.67 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS, FITNESS | Y | ST4030B | SUBMETER | MULTIPLY P1*0.10 | (WEL_ST32)*0.10 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS, NURSING | Y | ST4030C | SUBMETER | MULTIPLY P1*0.23 | (WEL_ST32)*0.23 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS, UPPSTREAM | N | ST4030D | VIRTUAL | SUBSTRACT P1 - (P2 + P3 + P4) | WEL_ST32, WEL_ST32*0.67, WEL_ST32*0.10, WEL_ST32*0.23 | BASED ON BLDG GSF | N
4031 | THE GLOBE | Student Success Building, Phase 2 | Y | ST4031 | BUILDING | SET POINT | STC2_ST32 |  | Y | ST4031_UTL_METER_DAY32 | Y
4060 | DORMAN HALL | Residents Hall # 10, Dorman Hall | Y | ST4060 | BUILDING | DIVIDED P1/2 | 4060_ST32 |  | Y | ST4060_UTL_METER_DAY32 | Y
4061 | DEVINEY HALL | Residents Hall # 11, Deviney Hall | Y | ST4061 | BUILDING | DIVIDE P1/2 | 4060_ST32 |  | N
4062 | AZALEA HALL | Residents Hall, Azalea Hall | Y | ST4062 | BUILDING | DIVIDE P1/2 | 4062_ST32 |  | Y | ST4062_UTL_METER_DAY32 | Y
4062 | AZALEA HALL | Azalea Hall Food Service | Y | ST4062A | BUILDING | SET EQUAL TO | 4062_FS2_ST32 |  | Y | ST4062A_UTL_METER_DAY32 | Y
4063 | MAGNOLIA HALL | Residents Hall, Magnolia Hall | Y | ST4063 | BUILDING | DIVIDE P1/2 | 4062_ST32 |  | N
Total |  | 1 | [8 empty] | 1
ALL OF THE ALIAS ARE IN DESIGO

## CHILLED WATER
UTILITIES BILLING
CHILLED WATER
BLDG # | BLDG NAME | CUSTOMER | BILLED IN AIM (Y/N) | METER ID | METER TYPE | CALC | BAS POINT NAME(S) | NOTES | NEED ALIAS? (Y/N) | ALIAS | ALIAS IN DESIGO? (Y/N)
0000 |  | PRIMARY CW METER | N | CW0000 | MASTER | ADD P1, P2, P3, P4 | PLANT1_TN32, SP1_TN32, STP_TN32, SP2_TN32 | PLANT1_TN32 NOT BE USED ANY MORE. CHECK CUP_TN32 INSTEAD. | Y | CW0000.1_UTL_METER_DAY32, CW0000.2_UTL_METER_DAY32, CW0000.3_UTL_METER_DAY32, CW0000.4_UTL_METER_DAY32 | Y
0001 | WESTCOTT BUILDING | WESTCOTT, WETN32 | Y | CW0001 | BUILDING | SET EQUAL TO | WE_TN32 |  | Y | CW0001_UTL_METER_DAY32 | Y
0002 | DIFFENBAUGH BUILDING | DIFFENBAUGH, DITN32 | Y | CW0002 | BUILDING | SET EQUAL TO | DITN32 |  | Y | CW0002_UTL_METER_DAY32 | Y
0002 | DIFFENBAUGH BUILDING | DIFFENBAUGH, DITN32 | Y | CW0002A | BUILDING | SET EQUAL TO | DI_NODE_TN32 | This specific point is not in desigo, but the points for every month (ex. DI_NODE_TN33-44) are in desigo. | Y | CW0002A_UTL_METER_DAY32 | N
0003 | WILLIAMS BUILDING | WILLIAMS BLDG, WITN32 | Y | CW0003 | BUILDING | SET EQUAL TO | WITN32 |  | Y | CW0003_UTL_METER_DAY32 | Y
0004 | DODD HALL | DODD HALL, DHTN32 | Y | CW0004 | BUILDING | SET EQUAL TO | DH_TN32 |  | Y | CW0004_UTL_METER_DAY32 | Y
0005 | CRIMINOLOGY AND CRIMINAL JUSTICE BUILDING | EPPES HALL | Y | CW0005 | BUILDING | SET EQUAL TO | EPS_TN32 |  | Y | CW0005_UTL_METER_DAY32 | Y
0006 | KELLOGG BUILDING | KELLOGG RESEARCH, PRTN32 | Y | CW0006 | BUILDING | SET EQUAL TO | PRTN32 |  | Y | CW0006_UTL_METER_DAY32 | Y
0007 | FINE ARTS BUILDING | FINE ARTS, FATN32 | Y | CW0007 | BUILDING | SET EQUAL TO | FA_TN32 |  | Y | CW0007_UTL_METER_DAY32 | Y
0008 | BELLAMY BUILDING | BELLAMY, BETN32 | Y | CW0008 | BUILDING | SET EQUAL TO | BETN32 |  | Y | CW0008_UTL_METER_DAY32 | Y
0009 | BIOMEDICAL RESEARCH FACILITY | BIO MED RESEARCH, BMTN32 | Y | CW0009 | BUILDING | SET EQUAL TO | 0009_TN_32 |  | Y | CW0009_UTL_METER_DAY32 | Y
0011 | SHAW BUILDING (MAIN CAMPUS) | SHAW BLDG NEW, SHAW_TN32 | Y | CW0011 | BUILDING | SET EQUAL TO | SHAW_TN32 |  | Y | CW0011_UTL_METER_DAY32 | Y
0011 | SHAW BUILDING (MAIN CAMPUS) | SHAW BUILDING OLD, SHAW_OLD_TN32 | Y | CW0011A | BUILDING | SET EQUAL TO | SHAW_OLD_TN32 |  | Y | CW0011A_UTL_METER_DAY32 | Y
0012 | JENNIE MURPHREE HALL | JENNIE MURPHREE HALL, JMTN32 | Y | CW0012 | BUILDING | SET EQUAL TO | 0012_TN32 |  | Y | CW0012_UTL_METER_DAY32 | Y
0013 | REYNOLDS HALL | REYNOLDS HALL, RETN32 | Y | CW0013 | BUILDING | SET EQUAL TO | 0013_TN32 |  | Y | CW0013_UTL_METER_DAY32 | Y
0014 | BRYAN HALL | BRYAN HALL, BHTN32 | Y | CW0014 | BUILDING | SET EQUAL TO | 0014_TN32 | IT IS THE BACnet POINT, NOT THE APOGEE ONE | Y | CW0014_UTL_METER_DAY32 | Y
0015 | BROWARD HALL | BROWARD HALL, BRTN32 | Y | CW0015 | BUILDING | SET EQUAL TO | BRTN32 |  | Y | CW0015_UTL_METER_DAY32 | Y
0016 | GILCHRIST HALL | GILCHRIST HALL, GHTN32 | Y | CW0016 | BUILDING | SET EQUAL TO | GHTN32 |  | Y | CW0016_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON DINING, JO_EG_TN32 | Y | CW0017A | SUBMETER | SET EQUAL TO | JO_TENTN32 |  | Y | CW0017A_UTL_METER_DAY32 | Y
0017 | JOHNSTON BUILDING | JOHNSTON DINING, JO_TN32 | N | CW0017B | DISTRIBUTION | ADD P1 + P2 | JO_TN32, JO_TENTN32 |  | N
0017 | JOHNSTON BUILDING | JOHNSTON DINING, UPSTREAM METER | Y | CW0017C | VIRTUAL | SET EQUAL TO | JO_TN32 |  | N
0017 | JOHNSTON BUILDING | JOHNSTON NEW MIDDLE SECTION | Y | CW0017D | BUILDING | SET EQUAL TO | JB_TN32 |  | Y | CW0017D_UTL_METER_DAY32 | Y
0019 | SHORES BUILDING | LIBRARY SCIENCE, LSTN32 | Y | CW0019 | BUILDING | SET EQUAL TO | LS_TN32 |  | Y | CW0019_UTL_METER_DAY32 | Y
0020 | DIRAC SCIENCE LIBRARY | DIRAC SCIENCE LIBRARY, SCTN32 | Y | CW0020 | BUILDING | SET EQUAL TO | SCLT32 |  | Y | CW0020_UTL_METER_DAY32 | Y
0023 | ROVETTA BUILDING A | ROVETTA, A BNTN32 | Y | CW0023 | BUILDING | SET EQUAL TO | ROV_A_TN32 |  | Y | CW0023_UTL_METER_DAY32 | Y
0025 | MONTGOMERY | MONTGOMERY GYM, MGTN32 | Y | CW0025 | BUILDING | SET EQUAL TO | MGTN32 |  | Y | CW0025_UTL_METER_DAY32 | Y
0026 | LEACH CENTER | NATATORIUM, NATN32 | Y | CW0026 | BUILDING | SET EQUAL TO | NATN32 |  | Y | CW0026_UTL_METER_DAY32 | Y
0028 | THAGARD BUILDING | THAGARD HEALTH CTR, HCTN32 | Y | CW0028 | BUILDING | SET EQUAL TO | HCTN32 |  | Y | CW0028_UTL_METER_DAY32 | Y
0030 | CENTRAL UTILITIES PLANT | CENTRAL UTILITY PLANT, CUPTN office use | Y | CW0030 | BUILDING | SET EQUAL TO* | CUP_TN32 | THIS BAS POINT IS FOR CENTRAL PLANT CHILLERS AND NOT ONLY FOR OFFICE USE - POINT NOT UPLOADED TO DESIGO. could not find the point for this meter | Y | CW0030_UTL_METER_DAY32 | N
0035 | HOFFMAN TEACHING LAB | CHEMISTRY II, HOTN32 | N | CW0035 | DISTRIBUTION | SET EQUAL TO | HOTN32 |  | Y | CW0035_UTL_METER_DAY32 | Y
0035 | HOFFMAN TEACHING LAB | HOFFMAN UPSTREAM METER | Y | CW0035A | VIRTUAL | SUBSTRACT P1 - (P2 + P3) | HOTN32, OSTN32, FLTN32 |  | N
0036 | ROGERS BUILDING (OSB) | OCEANOGRAPHY STATISTICS, OSTN32 | Y | CW0036 | SUBMETER | SET EQUAL TO | OSTN32 |  | Y | CW0036_UTL_METER_DAY32 | Y
0037 | FISHER LECTURE HALL | FISHER HALL | Y | CW0037 | SUBMETER | SET EQUAL TO | FLTN32 |  | Y | CW0037_UTL_METER_DAY32 | Y
0038 | DITTMER CHEMISTRY LAB | CHEMISTRY I, DTTN32 | Y | CW0038 | BUILDING | SET EQUAL TO | DTTN32 |  | Y | CW0038_UTL_METER_DAY32 | Y
0039 | BIOLOGY UNIT I | BIOLOGY, BITN32 | Y | CW0039 | BUILDING | SET EQUAL TO | 0039_TN32 |  | Y | CW0039_UTL_METER_DAY32 | Y
0040 | DUXBURY HALL | SCHOOL OF NURSING, NRTN32 | Y | CW0040 | BUILDING | SET EQUAL TO | 0040_TN32 |  | Y | CW0040_UTL_METER_DAY32 | Y
0041 | KEEN BUILDING | KEEN, KETN32 | Y | CW0041 | BUILDING | SET EQUAL TO | KETN32 |  | Y | CW0041_UTL_METER_DAY32 | Y
0042 | COLLINS RESEARCH BUILDING | NUCLEAR RESEARCH, NUTN32 | Y | CW0042 | BUILDING | SET EQUAL TO | NUTN32 |  | Y | CW0042_UTL_METER_DAY32 | Y
0044 | ROGERS HALL | ROGERS HALL, ROTN32 | Y | CW0044 | BUILDING | SET EQUAL TO | RO_TN32 |  | Y | CW0044_UTL_METER_DAY32 | Y
0045 | RICHARDS BUILDING | UNDERGRAD LAB RICHARDS, RITN32 | Y | CW0045 | BUILDING | SET EQUAL TO | RITN32 |  | Y | CW0045_UTL_METER_DAY32 | Y
0046 | SALLEY HALL | SALLEY HALL, SLTN32 | Y | CW0046 | BUILDING | SET EQUAL TO | SH_TN32 |  | Y | CW0046_UTL_METER_DAY32 | Y
0050 | STONE BUILDING | STONE, STTN32 | Y | CW0050 | BUILDING | SET EQUAL TO | STN_TN32 |  | Y | CW0050_UTL_METER_DAY32 | Y
0052 | ROVETTA BUILDING B | BUSINESS, BWTN32 | Y | CW0052 | BUILDING | SET EQUAL TO | ROV_B_TN32 |  | Y | CW0052_UTL_METER_DAY32 | Y
0054 | HOUSEWRIGHT MUSIC BUILDING | NEW MUSIC HOUSEWRIGHT, NMTN32 | Y | CW0054 | BUILDING | SET EQUAL TO | 0054_TN32 |  | Y | CW0054_UTL_METER_DAY32 | Y
0055 | CAROTHERS HALL | EDUCATION CAROTHERS, EDTN32 | Y | CW0055 | BUILDING | SET EQUAL TO | ED_TN32 |  | Y | CW0055_UTL_METER_DAY32 | Y
0057 | PEPPER BUILDING | CLAUDE PEPPER, PBTN32 | Y | CW0057 | BUILDING | SET EQUAL TO | PBTN32 |  | Y | CW0057_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARKING GARAGE #1, PGTN32 | N | CW0070 | DISTRIBUTION | SET EQUAL TO | PGTN32 |  | Y | CW0070_UTL_METER_DAY32 | Y
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARKING GARAGE #1 | Y | CW0070A | SUBMETER | SET EQUAL TO | N/A | CALCULATED MANUALLY BY NARIMAN | Y | CW0070A_UTL_METER_DAY32 | N
0070 | PARKING GARAGE #1 - WOODWARD AVE | PARKING GARAGE #1, UPSTREAM METER | Y | CW0070B | VIRTUAL | SUBSTRACT P1 - P2 | PGTN32, N/A |  | N
0072 | LONGMIRE BUILDING | LONGMIRE, LOTN32 | Y | CW0072 | BUILDING | SET EQUAL TO | LOTN32 |  | Y | CW0072_UTL_METER_DAY32 | Y
0074 | LANDIS HALL | LANDIS HALL, LHTN32 | Y | CW0074 | BUILDING | SET EQUAL TO | LANDIS_TN32 |  | Y | CW0074_UTL_METER_DAY32 | Y
0075 | MCCOLLUM HALL | MCCOLLUM HALL, MCTN32 | Y | CW0075 | BUILDING | SET EQUAL TO | MH_TN32 |  | Y | CW0075_UTL_METER_DAY32 | Y
0076 | TANNER HALL | 840 W JEFFERSON PUBLIC SAFETY, PSTN32 | Y | CW0076 | BUILDING | SET EQUAL TO | PSTN32 |  | Y | CW0076_UTL_METER_DAY32 | Y
0077 | MENDENHALL BUILDING A | MENDENHALL MAINT BLDG A, MATN32 | Y | CW0077 | BUILDING | SET EQUAL TO | MATN32 |  | Y | CW0077_UTL_METER_DAY32 | Y
0085 | CAWTHON HALL | CAWTHON HALL, CAWTN32 | Y | CW0085 | BUILDING | SET EQUAL TO | CAWCTD32 |  | Y | CW0085_UTL_METER_DAY32 | Y
0089 | KUERSTEINER MUSIC BUILDING | MUSIC KURSTEINER, MSTN32 | Y | CW0089 | BUILDING | SET EQUAL TO | MS_TN32 |  | Y | CW0089_UTL_METER_DAY32 | Y
0113 | CARRAWAY BUILDING | CARRAWAY, CATN32 | Y | CW0113 | BUILDING | SET EQUAL TO | 0113_TN32 |  | Y | CW0113_UTL_METER_DAY32 | Y
0114 | ENGINEERING LAB BUILDING | ENGINEERING LAB BUILDING | Y | CW0114 | BUILDING | SET EQUAL TO | ENGLAB_TN32 |  | Y | CW0114_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE, LVTN32 | Y | CW0116 | BUILDING | SET EQUAL TO | LVTN32 |  | Y | CW0116_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE WEATHER STA ALL FLOORS, | N | CW0116A | DISTRIBUTION | SET EQUAL TO | NWTNA32 | THIS IS THE CORRECT POINT FOR DESIGO. HOWEVER, THIS FLOW METER IS FAULTY AND DOES NOT MATCH THE NUMBERS IN AIM (BEING MANUALLY CALCULATED BY NARIMAN) | Y | CW0116A_UTL_METER_DAY32 | Y
0116 | LOVE BUILDING | LOVE, NOAA FLOORS 4,5, NWD432 | Y | CW0116B | SUBMETER | MULTIPLY P1*0.6 | NWTNA32 |  | N |  | N
0116 | LOVE BUILDING | LOVE NOAA UPSTREAM METER | Y | CW0116C | VIRTUAL | MULTIPLY P1*0.4 | NWTNA32 |  | N
0121 | HARPE-JOHNSON BUILDING | ROTC | Y | CW0121C | BUILDING | SET EQUAL TO | 0121_TN32 |  | Y | CW0121C_UTL_METER_DAY32 | Y
0132 | TULLY GYM | TULLY GYM, TGTN32 | Y | CW0132 | BUILDING | SET EQUAL TO | TGTN32 |  | Y | CW0132_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STOZIER LIBRARY, SNTN32 | Y | CW0134 | BUILDING | SET EQUAL TO | SNTN32 |  | Y | CW0134_UTL_METER_DAY32 | Y
0134 | STROZIER LIBRARY | STROZIER LIBRARY, SSTN32 | Y | CW0134A | BUILDING | SET EQUAL TO | SSTN32 |  | Y | CW0134A_UTL_METER_DAY32 | Y
0135 | SANDELS BUILDING | SANDELS, SATN32 | Y | CW0135 | BUILDING | SET EQUAL TO | SATN32 |  | Y | CW0135_UTL_METER_DAY32 | Y
0146 | KASHA LABORATORY | IMB, IMBTN32 | Y | CW0146 | BUILDING | SET EQUAL TO | IMBTN32 |  | Y | CW0146_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UCC COMPLEX |  | CW0223 | DISTRIBUTION | SET EQUAL TO | STP_TN32 | THIS POINT IS USED FOR THE SUM OF THE MASTER AND ALREADY HAS A ALIAS (CW0000.3_UTL_METER_DAY32) | Y | CW0223_UTL_METER_DAY32 | Y
0223 | UNIVERSITY CENTER - BUILDING A | UCC COMPLEX UPSTREAM METER | Y | CW0223A | VIRTUAL | SUBSTRACT P1 - (P2 + P3 +P4) | STP_TN32, 0224_CLUB_TN32, 0224_ATHLETICS_TN32, NTPT32 |  | N
0224 | UNIVERSITY CENTER - BUILDING B | UNIV CENTER CLUB CORP, SL_LVL356_TN32 | Y | CW0224 | SUBMETER | MULTIPLY P1 * 0.4624 | UCB_NEW_TN32 * 0.4624 | points for every month follow different format 0224_CLUB_TN33-44 | Y | CW0224_UTL_METER_DAY32 | Y
0224 | UNIVERSITY CENTER - BUILDING B | UCB TOWERS EAST & WEST | Y | CW0224TWS | SUBMETER | MULTIPLY P1 * 0.5376 | UCB_NEW_TN32 * 0.5376 | points for every month follow different format: 0224_ATHLETICS_TN33-44 | N |  | N
0226 | UNIVERSITY CENTER - BUILDING D | COMM BLDG, TOTAL , NPTP32 | Y | CW0226 | SUBMETER | SET EQUAL TO | NTPT32 |  | Y | CW0226_UTL_METER_DAY32 | Y
0260 | ASKEW STUDENT LIFE CENTER | STUDENT LIFE, LITN32 | Y | CW0260 | BUILDING | SET EQUAL TO | LITN32 |  | Y | CW0260_UTL_METER_DAY32 | Y
0293 | HAZARDOUS WASTE FACILITY | HAZARDOUS WASTE | Y | CW0293 | BUILDING | SET EQUAL TO | N/A | THIS METER IS A MANUAL READ | Y | CW0293_UTL_METER_DAY32 | N
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, SV_TN32 | N | CW0379 | DISTRIBUTION | ADD P1, P2, P3, P4 | SV_LVL1_TN32, SV_LVL3_TN32, SV_LVL2_TN32, SV_LVL1A_TN32 |  | N
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, 1ST FL, SV_LVL1_TN32 | Y | CW0379A | SUBMETER | SET EQUAL TO | SV_LVL1_TN32 |  | Y | CW0379A_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, 3 FR, SV_LVL3_TN | Y | CW0379B | SUBMETER | SET EQUAL TO | SV_LVL3_TN32 |  | Y | CW0379B_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, 2 FL, SV_LVL2_TN | Y | CW0379C | SUBMETER | SET EQUAL TO | SV_LVL2_TN32 |  | Y | CW0379C_UTL_METER_DAY32 | Y
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, DINER, SV_LVL1A_TN | Y | CW0379D | SUBMETER | SET EQUAL TO | SV_LVL1A_TN32 |  | Y | CW0379D_UTL_METER_DAY32 | N
0379 | STUDENT SERVICES BUILDING | STUDENT SVR, UPSTREAM METER | N | CW0379E | VIRTUAL | SUBSTRACT P1 - (P2 + P3 + P4 + P5) | (SV_LVL1_TN32, SV_LVL3_TN32, SV_LVL2_TN32, SV_LVL1A_TN32) , SV_LVL1_TN32, SV_LVL3_TN32, SV_LVL2_TN32, SV_LVL1A_TN32 |  | N
0488 | SEMINOLE CAFE RESTURANT | WEST CAMPUS DINING, WDINING_TN32 | Y | CW0488 | BUILDING | SET EQUAL TO | WDINING_TN32 |  | Y | CW0488_UTL_METER_DAY32 | Y
0495 | RAGANS HALL 1 (A) | NEW RESIDENCE HALL BLDG A, REATN32 | Y | CW0495 | BUILDING | SET EQUAL TO | REATN32 |  | Y | CW0495_UTL_METER_DAY32 | Y
0496 | RAGANS HALL 2 (B) | NEW RESIDENCE HALL BLDG B, REBTN32 | Y | CW0496 | BUILDING | SET EQUAL TO | REBTN32 |  | Y | CW0496_UTL_METER_DAY32 | Y
0497 | RAGANS HALL 3 (C) | NEW RESIDENCE HALL BLDG C, RECTN32 | Y | CW0497 | BUILDING | SET EQUAL TO | RECTN32 |  | Y | CW0497_UTL_METER_DAY32 | Y
0498 | RAGANS HALL 4 (D) | NEW RESIDENCE HALL BLDG D, RECTN32 | Y | CW0498 | BUILDING | SET EQUAL TO | REDTN32 |  | Y | CW0498_UTL_METER_DAY32 | Y
4001 | COLLEGE OF MEDICINE - THRASHER BUILDING | MEDICAL SCHOOL, MED_SCH_TN32 | Y | CW4001 | BUILDING | SET EQUAL TO | MED_SCH_TN32 |  | Y | CW4001_UTL_METER_DAY32 | Y
4004 | PSYCHOLOGY DEPARTMENT BUILDING | NEW PSY BLDG.& AUD & Phase 2 | Y | CW4004 | BUILDING | SET EQUAL TO | PSY_TN32 |  | Y | CW4004_UTL_METER_DAY32 | Y
4007 | KING LIFE SCIENCE BUILDING | LIFE SCIENCES | Y | CW4007 | BUILDING | SET EQUAL TO | LIFE_TN32 |  | Y | CW4007_UTL_METER_DAY32 | Y
4008 | CHEMICAL SCIENCE LABORATORIES | NEW CHEMISTRY BLDG | Y | CW4008 | BUILDING | SET EQUAL TO | CHEM_TN32 |  | Y | CW4008_UTL_METER_DAY32 | Y
4009 | CLASSROOM BUILDING (HCB) | CLASSROOM BLDG. | Y | CW4009 | BUILDING | SET EQUAL TO | CLASS_TN32 |  | Y | CW4009_UTL_METER_DAY32 | Y
4010 | EOAS BUILDING | EAOS BLDG. | Y | CW4010 | BUILDING | SET EQUAL TO | 4010_TN32 |  | Y | CW4010_UTL_METER_DAY32 | Y
4011 | DUNLAP SUCCESS CENTER | STUDENT SUCCESS BUILDING (DUNLAP) | Y | CW4011 | BUILDING | SET EQUAL TO | STSC_TN32 |  | Y | CW4011_UTL_METER_DAY32 | Y
4018 | NEW STUDENT UNION | NEW STUDENT UNION ENTIRE COMPLEX | Y | CW4018 | BUILDING | MULTIPLY P1*0.35 | 4018_CHW_TONS32 | THIS METER IS AN ESTIMATION OF THE SUM OF ALL THREE METERS FOR THE UNION BILLED IN AIM. | Y | CW4018_UTL_METER_DAY32 | Y
| NEW STUDENT UNION | FOLLETT-BOOKSTORE | Y | CW4018A | BUILDING | MULTIPLY P1*0.34 | 4018_CHW_TONS32 |  | N
| NEW STUDENT UNION | FOOD SERVICE COMBINED | Y | CW4018B | BUILDING | MUTLIPL.Y P1*0.31 | 4018_CHW_TONS32 |  | N
4020 | WILDWOOD HALLS 1 | New Residents Hall # 5, Wildwood dr. South | Y | CW4020 | BUILDING | SET EQUAL TO | WILD_S_TN32 |  | Y | CW4020_UTL_METER_DAY32 | Y
4021 | WILDWOOD HALLS 2 | New Residents Hall # 6, Wildwood dr. North | Y | CW4021 | BUILDING | SET EQUAL TO | WILD_N_TN32 |  | Y | CW4021_UTL_METER_DAY32 | Y
4022 | TRADITIONS HALL | TRADITIONS HALL | Y | CW4022 | BUILDING | SET EQUAL TO | WILD_3_TN32 |  | Y | CW4022_UTL_METER_DAY32 | Y
4023 | DEGRAFF HALL EAST | DEGRAFF HALL #8 | Y | CW4023 | BUILDING | SET EQUAL TO | DEG_E_TN32 |  | Y | CW4023_UTL_METER_DAY32 | Y
4024 | DEGRAFF HALL WEST | DEGRAFF HALL #9 | Y | CW4024 | BUILDING | SET EQUAL TO | DEG_W_TN32 |  | Y | CW4024_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, total usage | N | CW4029 | DISTRIBUTION | SET EQUAL TO | JBA_TN32 |  | Y | CW4029_UTL_METER_DAY32 | Y
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, Chick-fil-a | Y | CW4029A | SUBMETER | MULTIPLY P1*0.122995 | JBA_TN32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, Rising Roll | Y | CW4029B | SUBMETER | MULTIPLY P1*0.161551 | JBA_TN32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, POD | Y | CW4029C | SUBMETER | MULTIPLY P1*0.067846 | JBA_TN32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, E&G | Y | CW4029D | SUBMETER | MULTIPLY P1*0.647608 | JBA_TN32 | BASED ON BLDG GSF | N
4029 | HONORS SCHOLARS & FELLOWS | Johnston Building Annex, Remainder | N | CW4029E | VIRTUAL | SUBSTRACT P1 - (P2 + P3 + P4 + P5) | JBA_TN32, (JBA_TN32)*0.122995, (JBA_TN32)*0.161551, (JBA_TN32)*0.067846, (JBA_TN32)*0.647608 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS CENTER BUILDING METER | N | CW4030 | DISTRIBUTION | SET EQUAL TO | WEL_TN32 |  | Y | CW4030_UTL_METER_DAY32 | Y
4030 | COBURN WELLNESS CENTER | WELLNESS, HEALTH | Y | CW4030A | SUBMETER | MULTIPLY P1*0.67 | (WEL_TN32)*0.67 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS, FITNESS | Y | CW4030B | SUBMETER | MULTIPLY P1*0.10 | (WEL_TN32)*0.10 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS, NURSING | Y | CW4030C | SUBMETER | MULTIPLY P1*0.23 | (WEL_TN32)*0.23 | BASED ON BLDG GSF | N
4030 | COBURN WELLNESS CENTER | WELLNESS, UPSTREAM | N | CW4030D | VIRTUAL | SUBSTRACT P1 - (P2 + P3 +P4) | WEL_TN32, (WEL_TN32)*0.67, (WEL_TN32)*0.10, (WEL_TN32)*0.23 | BASED ON BLDG GSF | N
4031 | THE GLOBE | Student Success Building, Phase 2 | Y | CW4031 | BUILDING | SET EQUAL TO | STC2_TN32 |  | Y | CW4031_UTL_METER_DAY32 | Y
4060 | DORMAN HALL | Residents Hall # 10, Dorman Hall | Y | CW4060 | BUILDING | SET EQUAL TO | 4060_TN32 |  | Y | CW4060_UTL_METER_DAY32 | Y
4061 | DEVINEY HALL | Residents Hall # 11, Deviney Hall | Y | CW4061 | BUILDING | SET EQUAL TO | 4061_TN32 |  | Y | CW4061_UTL_METER_DAY32 | Y
4062 | AZALEA HALL | Residents Hall, Azalea Hall | Y | CW4062 | BUILDING | SET EQUAL TO | 4062_CWTN32 |  | Y | CW4062_UTL_METER_DAY32 | Y
4062 | AZALEA HALL | Azalea Hall Food Service | Y | CW4062A | BUILDING | SET EQUAL TO | 4062_FS_TN32 |  | Y | CW4062A_UTL_METER_DAY32 | Y
4063 | MAGNOLIA HALL | Residents Hall, Magnolia Hall | Y | CW4063 | BUILDING | SET EQUAL TO | 4063_CWTN32 |  | Y | CW4063_UTL_METER_DAY32 | Y
4090 | INDOOR PRACTICE FACILITY | Indoor Practice Facility | Y | CW4090 | BUILDING | SET EQUAL TO | STP_CWT_32 |  | Y | CW4090_UTL_METER_DAY32 | Y
|  | 119 |  | 119 | [6 empty] | 100
ALL OF THE ALIAS ARE IN DESIGO
Note on K5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Alias manually input. This meter consists of FOUR BAS points. They are all aliased and differentiated by using .1, .2, .3, .4 at the end of the alias.

## PROPERTIES (hidden)
Property | Description | Address 1 | GSF
0001 | WESTCOTT BUILDING | 222 S COPELAND ST | 155315
0002 | DIFFENBAUGH BUILDING | 625 UNIVERSITY WAY | 97489
0003 | WILLIAMS BUILDING | 631 UNIVERSITY WAY | 70962
0004 | DODD HALL | 641 UNIVERSITY WAY | 54338
0005 | CRIMINOLOGY AND CRIMINAL JUSTICE BUILDING | 112 S COPELAND ST | 28752
0006 | KELLOGG BUILDING | 108 S COPELAND ST | 46323
0007 | FINE ARTS BUILDING | 530 W CALL ST | 122055
0008 | BELLAMY BUILDING | 113 COLLEGIATE LOOP | 157913
0009 | BIOMEDICAL RESEARCH FACILITY | 107 CHIEFTAN WAY | 58147
0010 | TURNBULL CONFERENCE CENTER | 555 W PENSACOLA ST | 73299
0011 | SHAW BUILDING (MAIN CAMPUS) | 644 W CALL ST | 24635
0012 | JENNIE MURPHREE HALL | 126 CONVOCATION WAY | 74991
0013 | REYNOLDS HALL | 134 CONVOCATION WAY | 71650
0014 | BRYAN HALL | 182 CONVOCATION WAY | 36795
0015 | BROWARD HALL | 668 UNIVERSITY WAY | 38001
0016 | GILCHRIST HALL | 702 UNIVERSITY WAY | 65701
0017 | JOHNSTON BUILDING | 143 HONORS WAY | 181329
0018 | PUBLIC BROADCAST CENTER | 1600 RED BARBER PLAZA | 53013
0019 | SHORES BUILDING | 142 COLLEGIATE LOOP | 53543
0020 | DIRAC SCIENCE LIBRARY | 110 N WOODWARD AVE | 109662
0021 | ARCHIVED RECORD - HANDBALL COURTS
0022 | NATIONAL HIGH MAGNETIC FIELD LABORATORY - GENERAL SCIENCE | 1800 EAST PAUL DIRAC DR | 201654
0023 | ROVETTA BUILDING A | 821 ACADEMIC WAY | 67518
0024 | BUILDING 24 - WOODWARD ST. | 210 SOUTH WOODWARD S | 1919
0025 | MONTGOMERY | 130 COLLEGIATE LOOP | 94628
0026 | LEACH CENTER | 118 VARSITY WAY | 140990
0028 | THAGARD BUILDING | 109 COLLEGIATE LOOP | 44919
0029 | DEGRAFF (MARK H.) HALL | 700 WEST TENNESSEE ST | 30987
0030 | CENTRAL UTILITIES PLANT | 990 LEARNING WAY | 23737
0031 | C3 CONVENIENCE STORE - OLD FIRE SYSTEMS | 100 S WOODWARD ST | 1006
0032 | COLLEGE OF LAW - B.K. ROBERTS HALL | 425 W JEFFERSON ST | 72869
0033 | SATELLITE UTILITIES PLANT 1 | 1103 W CALL ST | 5940
0034 | ART EDUCATION ANNEX | 1025 W CALL ST | 1525
0035 | HOFFMAN TEACHING LAB | 101 CHIEFTAN WAY | 72344
0036 | ROGERS BUILDING (OSB) | 117 N WOODWARD AVE | 54794
0037 | FISHER LECTURE HALL | 111 N WOODWARD AVE | 8595
0038 | DITTMER CHEMISTRY LAB | 95 CHIEFTAN WAY | 144881
0039 | BIOLOGY UNIT I | 89 CHIEFTAN WAY | 80795
0040 | DUXBURY HALL | 98 VARSITY WAY | 65833
0041 | KEEN BUILDING | 77 CHIEFTAN WAY | 81056
0042 | COLLINS RESEARCH BUILDING | 1060 ATOMIC WAY | 53549
0043 | OLD DEVINEY HALL | 806 UNIVERSITY WAY | 65222
0044 | ROGERS HALL | 1147 ACADEMIC WAY | 66127
0045 | RICHARDS BUILDING | 1055 ATOMIC WAY | 26060
0046 | SALLEY HALL | 1106 W CALL ST | 125176
0047 | COLLEGE OF LAW - RESEARCH CENTER (LIBRARY) | 425 W JEFFERSON ST | 56891
0048 | COLLEGE OF LAW - ROTUNDA | 425 W JEFFERSON ST | 20273
0049 | DODD LECTURE HALL | 646 W JEFFERSON ST | 12329
0050 | STONE BUILDING | 1114 W CALL ST | 126189
0051 | OGLESBY UNION - TURNER BUILDING | 75 N WOODWARD AVE | 22523
0052 | ROVETTA BUILDING B | 821 ACADEMIC WAY | 74705
0053 | KELLUM HALL | 74 CHIEFTAN WAY | 116943
0054 | HOUSEWRIGHT MUSIC BUILDING | 122 N COPELAND ST | 107320
0055 | CAROTHERS HALL | 1021 ATOMIC WAY | 68221
0056 | OPERA SCENE SHOP | 1809 ROBERTS AVE | 7355
0057 | PEPPER BUILDING | 636 W CALL ST | 43121
0058 | GOLF COURSE - DRIVING RANGE | 2530 POTTSDAMER ST | 195
0059 | GOLF COURSE - RESTROOM | 2530 POTTSDAMER ST | 149
0061 | NATIONAL HIGH MAGNETIC FIELD LABORATORY - STORAGE BUILDING | 1800 E PAUL DIRAC DR | 4941
0062 | MIDDLETON GOLF CENTER | 2550 POTTSDAMER ST | 29725
0063 | GOLF COURSE - MAINTENANCE | 2000 WEST ORANGE AVE | 5539
0064 | FARM - THEATER SCENE STORAGE | 1907 UNIVERSITY FARM RD | 5283
0065 | FARM - RADIATION STORAGE | 1905 UNIVERSITY FARM RD | 4935
0066 | FARM - LAB ANIMAL RESOURCES | 1903 UNIVERSITY FARM RD | 5545
0067 | FARM - STORAGE BLDG. | 1901A UNIVERSITY FARM RD | 1629
0068 | FARM - ANIMAL PEN | 1901B UNIVERSITY FARM RD | 2634
0069 | NATIONAL HIGH MAGNETIC FIELD LABORATORY - DC MAGNET BUILDING | 1800 EAST PAUL DIRAC DR | 98962
0070 | PARKING GARAGE #1 - WOODWARD AVE | 104 N WOODWARD AVE | 304921
0071 | OLD FOOTBALL OBSERVATION TOWER | 475 WEST STADIUM DR | 300
0072 | LONGMIRE BUILDING | 125 CONVOCATION WAY | 39233
0073 | REGIONAL REHABILITATION CENTER | 166 LEON LANE | 36320
0074 | LANDIS HALL | 714 UNIVERSITY WAY | 106835
0075 | MCCOLLUM HALL | 1165 ACADEMIC WAY | 87574
0076 | TANNER HALL | 830 W JEFFERSON ST | 26276
0077 | MENDENHALL BUILDING A | 969 LEARNING WAY | 84663
0078 | MENDENHALL BUILDING B | 965 LEARNING WAY | 17523
0079 | SPEICHER TENNIS CENTER | 121 CHIEFTAN WAY | 10290
0080 | PRESIDENT'S POOL HOUSE | 1030 W TENNESSEE ST
0081 | CHI OMEGA-661 W JEFFERSON ST | 661 W JEFFERSON ST
0082 | KAPPA DELTA-555 W JEFFERSON ST | 555 W JEFFERSON ST
0083 | DELTA GAMMA-143 N COPELAND ST | 143 N COPELAND ST
0084 | ALPHA CHI OMEGA-518 W PARK | 518 WEST PARK AVE.
0085 | CAWTHON HALL | 119 HONORS WAY | 93987
0086 | PEARL TYNER WELCOME CENTER | 1030 W TENNESSEE ST | 4739
0087 | INTENSIVE ENGLISH - 918 W.PARK | 918 WEST PARK AVE. | 4420
0088 | NURSERY - GROUNDS GREENHOUSE | 1800 WEST ORANGE AVENUE | 3145
0089 | KUERSTEINER MUSIC BUILDING | 114 N COPELAND ST | 91889
0090 | ATHLETIC TRAINERS FACILITY | 124 CHIEFTAN WAY
0091 | MCINTOSH TRACK & FIELD BUILDING | 1104 SPIRIT WAY | 21231
0092 | ALLIGATOR PT. - LAB BUILDING | 1400 CO. RD. 370 | 2979
0093 | ALLIGATOR PT. - STORAGE | 1400 CO. RD. 370 | 1264
0095 | ALLIGATOR PT. - SHOP | 1400 CO. RD. 370 | 829
0099 | ALLIGATOR PT. - GARAGE | 1400 CO. RD. 370 | 965
009A | ECLIPSE TEST BUILDING | TEST LOCATION
009B | TEST BUILDING 009B | TEST LOCATION
0100 | CAMPBELL STADIUM | 411 STADIUM DR | 592320
0101 | ALLIGATOR POINT - PRESIDENT'S COTTAGE | 1396 ALLIGATOR DR | 2205
0102 | SMITH HALL | 78 CHIEFTAN WAY | 104789
0103 | COTTAGE (MABRY BLDG.) AT PRES. HOUSE | 1030 W TENNESSEE ST
0107 | INTERNATIONAL STUDENTS HOUSE | 108 S WILDWOOD DR | 8708
0108 | PHI KAPPA TAU-108 S WILDWOOD | 112 S WILDWOOD DR | 8270
0112 | OLD DORMAN HALL | 812 W JEFFERSON ST | 139736
0113 | CARRAWAY BUILDING | 60 N WOODWARD AVE | 41428
0114 | ENGINEERING LAB BUILDING | 1033 ATOMIC WAY | 9476
0115 | HOWSER STADIUM | 270 CHIEFTAN WAY | 75788
0116 | LOVE BUILDING | 1017 ACADEMIC WAY | 101107
0117 | HASKIN CIRCUS COMPLEX | 269 CHIEFTAN WAY | 6072
0120 | TRACK STORAGE & RESTROOMS | 1104 SPIRIT WAY | 1153
0121 | HARPE-JOHNSON BUILDING | 103 VARSITY WAY | 20595
0122 | TRACK PRESS BOX AND BLEACHERS | 350 CHIEFTAN WAY | 257
0123 | COM123-STUDENT COMMUNITY&LABS | 1249 W CALL ST
0125 | COM125-IMB OFFICES & LABS | 1249 W CALL ST
0130 | COM130-ATLETICS TEMP GYM | 315 W STADIUM DR
0132 | TULLY GYM | 139 CHIEFTAN WAY | 91893
0133 | CONRADI (EDWARD) BUILDING | 707 PALMETTO DRIVE | 70403
0134 | STROZIER LIBRARY | 116 HONORS WAY | 229492
0135 | SANDELS BUILDING | 120 CONVOCATION WAY | 70031
0139 | 208-210 N WOODWARD-DEMETREE | 84 S WILDWOOD DR
0140 | 204-206 N WOODWARD-DEMETREE | 86 S WILDWOOD DR
0141 | EINSTEIN BROS BAGELS | 977 LEARNING WAY | 1988
0142 | LONG TRACK RESTROOMS | 350 CHIEFTAN WAY | 1160
0143 | WOMAN'S SOFTBALL FACILITY - VARSITY DR. | VARSITY DR
0144 | TV TOWER | 6559 SMITH CREEK RD | 1
0146 | KASHA LABORATORY | 91 CHIEFTAN WAY | 50802
0147 | ETV TRANSMITTER BUILDING | FOREST | 1460
0150 | ALUMNI VL1 | 150 BLISS DR | 12114
0151 | ALUMNI VL1 | 151 BLISS DR | 12114
0152 | ALUMNI VL1 | 152 BLISS DR | 12114
0153 | ALUMNI VL1 | 153 BLISS DR | 12114
0154 | ALUMNI VL1 | 154 HERLONG DR | 12114
0155 | ALUMNI VL1 | 155 HERLONG DR | 12114
0156 | ALUMNI VL1 | 156 HERLONG DR | 12114
0157 | FACILITIES CAMPUS SUPPORT | 157 HERLONG DR | 12845
0158 | ALUMNI VL1 | 158 HERLONG DR | 12114
0159 | ALUMNI VL1 | 159 HERLONG DR | 12114
0160 | ALUMNI VL1 | 160 CRENSHAW DR | 12114
0161 | ALUMNI VL1 | 161 CRENSHAW DR | 12114
0162 | ALUMNI VL1 | 162 CRENSHAW DR | 12114
0163 | ALUMNI VL1 | 163 CRENSHAW DR | 12114
0164 | ALUMNI VL1 | 164 CRENSHAW DR | 12114
0165 | ALUMNI VL1 | 165 CRENSHAW DR | 12114
0166 | ALUMNI VL1 | 166 CRENSHAW DR | 12114
0167 | ALUMNI VL1 | 167 CRENSHAW DR | 12114
0168 | ALUMNI VL LAUNDRY-REC.CTR. | 168 CRENSHAW DR | 7380
0169 | FSU POLICE DEPARTMENT UNIT 3 | 169 HERLONG DR | 7157
0170 | ALUMNI VILLAGE MAINTENANCE SHED-USED BY GROUNDS | 170 HERLONG DR | 1907
0171 | ALUMNI VL2 | LEVY AVENUE | 6924
0172 | ALUMNI VL2 | LEVY AVENUE | 7934
0173 | ALUMNI VL2 | LEVY AVENUE | 9650
0174 | ALUMNI VL2 | LEVY AVENUE | 5654
0175 | ALUMNI VL2 | 175 BRITTAIN DR | 6360
0176 | ALUMNI VL2 | LEVY AVENUE | 7934
0177 | ALUMNI VL2 | 177 BRITTAIN DR | 6554
0178 | ALUMNI VL2 | LEVY AVENUE | 5204
0179 | ALUMNI VL2 | 179 PENNELL CIR | 5244
0180 | ALUMNI VL2 | 180 CRENSHAW CT S | 9350
0181 | ALUMNI VL2 | 181 CRENSHAW CT S | 7570
0182 | ALUMNI VL2 | 182 PENNELL CIR | 8100
0183 | ALUMNI VL2 | 183 PENNELL CIR | 8100
0184 | ALUMNI VL2 | 184 PENNELL CIR | 6924
0185 | ALUMNI VL2 | 185 CRENSHAW DR | 6500
0186 | ALUMNI VL2 | 186 CRENSHAW DR | 6468
0187 | ALUMNI VL2 | 187 CRENSHAW CT N | 6924
0188 | ALUMNI VL2 | 188 CRENSHAW CT N | 3240
0189 | ALUMNI VL2 | 189 CRENSHAW CT N | 7644
0190 | ALUMNI VL2 | 190 CRENSHAW CT N | 8174
0193 | OGLESBY UNION - CRENSHAW BLDG. | 91 N WOODWARD AVE | 14742
0194 | OGLESBY UNION - ACTIVITIES | 87 N WOODWARD AVE | 47300
0195 | MOORE AUDITORIUM. | 83 N WOODWARD AVE | 12536
0196 | OGLESBY UNION - DAVIS BUILDING | 79 N WOODWARD AVE | 60936
0197 | STULTS AQUATIC CNT. - POOL | 81 S WILDWOOD DR
0198 | STULTS AQUATIC CNT. - LOCKERS | 81 WILDWOOD DR
0199 | OGLESBY UNION - POST OFFICE BUILDING | 71 N WOODWARD AVE | 26690
0200 | MOORE(COYLE E. SR)ATHLETIC CNT | 525 STADIUM DRIVE | 65085
0201 | STORAGE TRAILER - IMB | 1229 W CALL ST
0202 | COLLEGE OF LAW - VILLAGE GREEN - HOBBY-HARRISON/CAWTHON HOUSE | 302 S M L KING JR BLVD | 2330
0203 | COLLEGE OF LAW - VILLAGE GREEN - CALDWELL HOUSE | 312 S M L KING JR BLVD | 5185
0204 | COLLEGE OF LAW - VILLAGE GREEN - DAMON HOUSE | 304 S M L KING JR BLVD | 3678
0205 | COLLEGE OF LAW - VILLAGE GREEN - AUSLEY HOUSE | 310 S M L KING JR BLVD | 3665
0211 | CPE 1 - DUNWOODY STREET | 408 DUNWOODY ST | 667
0213 | CPE 2 - DUNWOODY STREET | 410 DUNWOODY ST | 667
0215 | MISSION ROAD - MABRY BLDG. 1 | 2606 MISSION RD | 1162
0217 | MISSION ROAD - MABRY BLDG. 2 | 2606 MISSION RD | 1815
0220 | BUS STOP - NORTHSIDE ACAD.WAY | 824 ACADEMIC WAY | 84
0223 | UNIVERSITY CENTER - BUILDING A | 282 CHAMPIONS WAY | 251758
0224 | UNIVERSITY CENTER - BUILDING B | 288 CHAMPIONS WAY | 83457
0225 | UNIVERSITY CENTER - BUILDING C | 296 CHAMPIONS WAY | 264531
0226 | UNIVERSITY CENTER - BUILDING D | 403 STADIUM DR | 212336
0230 | MISSION ROAD - NEW GREENHOUSE | 2606 MISSION RD | 2188
0232 | POSTAL SERVICE STORAGE BLDG. | 609 W ST. AUGUSTINE ST | 150
0234 | COM234 - STORAGE | 317 WEST STADIUM DRI
0237 | CENTRAL UTILITIES PLANT STORAGE | 990 LEARNING WAY | 290
0238 | CENTRAL UTILITIES PLANT FUEL PUMP BUILDING | 990 LEARNING WAY | 100
0240 | MARCHING CHIEFS TOWER & FIELD | 265 CHIEFTAN WAY | 250
0241 | PORTABLE BUILDING | 2722 PLANT STREET
0242 | COM242-FACILITIES OFFICES | COLLEGE & COPELAND
0244 | COM244-CONSTRUCTION MANAGEMENT | 1229 W CALL ST
0245 | COM245-SSTRIDE PROGRAM | 1249 W CALL ST
0246 | COM246-IMB OFFICES | 1249 W CALL ST
0247 | COM247-MED ADMIN. & LIBRARY | 1269 W CALL ST
0248 | COM248-STORAGE | COLLEGE & COPELAND
0249 | ZONE 3 MAINTENANCE | 1187 ACADEMIC WAY | 1666
0250 | DRS - COMMONS BLDG | W CALL ST
0253 | MED SCHOOL TRAILER | 303 STADIUM DRIVE
0254 | SPORTS CLUBS FIELDS FACILITY | 1001 W ST. AUGUSTINE ST | 2763
0255 | WESTCOTT WELCOME CENTER | 537 W COLLEGE AVE | 154
0258 | GATE CONTROL BOOTH - UNIVERSITY CENTER | 291 CHAMPIONS WAY | 51
0260 | ASKEW STUDENT LIFE CENTER | 942 LEARNING WAY | 60944
0262 | MARINE LAB- GRADUATE OFFICE | 3618 COASTAL HIGHWAY 98 | 1338
0264 | MABRY BUILDING - #0264 | 1151 HULL DR | 1682
0269 | NATIONAL HIGH MAGNETIC FIELD LABORATORY - NMR BUILDING | 1800 EAST PAUL DIRAC DR | 29941
0270 | CHILD CARE CENTER | 1173 HULL DR | 4068
0271 | MODULAR 6 - MATH DEPARTMENT | 1167 HULL DR | 2507
0276 | RESERVATION-GARAGE | 3226 FLASTACOWO RD | 225
0277 | REZ GATE HOUSE | 3226 FLASTACOWO RD | 80
0278 | REZ CARETAKER'S RESIDENCE | 3226 FLASTACOWO RD | 1143
0279 | REZ STORAGE - CABIN 6 | 3226 FLASTACOWO RD | 591
0280 | REZ ADMINISTRATION BUILDING | 3226 FLASTACOWO RD | 2131
0281 | REZ WATERFRONT & OP OPERATIONS | 3226 FLASTACOWO RD | 3377
0282 | REZ CONFERENCE CENTER - CABIN 4 | 3226 FLASTACOWO RD | 5971
0283 | REZ DOCK COVER | 3226 FLASTACOWO RD | 957
0284 | REZ RECREATION BUILDING | 3226 FLASTACOWO RD | 4014
0285 | REZ STAFF RESIDENCE - CABIN 5 | 3226 FLASTACOWO RD | 591
0286 | REZ DORM - CABIN 6 | 3226 FLASTACOWO RD | 1197
0287 | REZ DORM - CABIN 7 | 3226 FLASTACOWO RD | 1197
0288 | REZ BOAT HOUSE | 3226 FLASTACOWO RD | 1640
0289 | REZ STORAGE - CABIN 7 | 3226 FLASTACOWO RD | 591
0291 | 118 N.WOODWARD (WELLNESS CONTRACTOR) | 118 N WOODWARD AVE | 2934
0292 | FLAMMABLE STORAGE | 965 LEARNING WAY | 255
0293 | HAZARDOUS WASTE FACILITY | 965 LEARNING WAY | 1327
0294 | HECHT HOUSE | 634 W CALL ST | 16970
0295 | WAREHOUSE - PROPERTY RECORDS 1 | 1801 ROBERTS AVE | 7051
0296 | CTR. FOR CIVIC ED.(930 W.PARK) | 930 WEST PARK AVE. | 4934
0297 | WAREHOUSE - PROPERTY RECORDS 2 | 1803 ROBERTS AVE | 6910
0298 | WAREHOUSE - HOUSING STORAGE 1 | 1805 ROBERTS AVE | 7030
0299 | WOMEN'S CENTER | 112 N WOODWARD ST | 2360
0300 | WAREHOUSE - HOUSING STORAGE 2 | 1807 ROBERTS AVE | 7079
0301 | ALUMNI VL3 | 301 PENNELL CIR | 6455
0302 | ALUMNI VL3 | 302 PENNELL CIR | 4370
0303 | ALUMNI VL3 | 303 PENNELL CIR | 4370
0304 | ALUMNI VL3 | 304 PENNELL CIR | 6455
0305 | ALUMNI VL3 | 305 PENNELL CIR | 3584
0306 | ALUMNI VL3 | 306 PENNELL CIR | 6600
0307 | ALUMNI VL3 | 307 PENNELL CIR | 6600
0308 | ALUMNI VL3 | 308 PENNELL CIR | 6600
0309 | ALUMNI VL3 | 309 PENNELL CIR | 3584
0310 | ALUMNI VL3 | 310 PENNELL CIR | 6600
0311 | ALUMNI VL3 | 311 PENNELL CIR | 1792
0312 | ALUMNI VL3 | 312 PENNELL CIR | 2688
0313 | ALUMNI VL3 | 313 PENNELL CIR | 6600
0314 | ALUMNI VL3 | 314 PENNELL CIR | 4950
0315 | ALUMNI VL3 | 315 PENNELL CIR | 1792
0316 | ALUMNI VL3 | 316 PENNELL CIR | 1792
0317 | ALUMNI VILLAGE-LAUNDRY-OFFICE | 317 PENNELL CIR | 2400
0318 | ALUMNI VL3 | 318 PENNELL CIR | 4950
0319 | ALUMNI VL3 | 319 PENNELL CIR | 4950
0320 | ALUMNI VL3 | 320 PENNELL CIR | 1792
0321 | ALUMNI VL3 | 321 PENNELL CIR | 1762
0322 | ALUMNI VL3 | 322 PENNELL CIR | 1792
0323 | ALUMNI VL3 | 323 PENNELL CIR | 896
0324 | ALUMNI VL3 | 324 PENNELL CIR | 3300
0325 | ALUMNI VL3 | 325 PENNELL CIR | 4950
0326 | ALUMNI VL3 | 326 PENNELL CIR | 2688
0327 | ALUMNI VL3 | 327 PENNELL CIR | 2688
0328 | ALUMNI VL3 | 328 PENNELL CIR | 4950
0329 | FSU POLICE DEPARTMENT UNIT 1 | 329 PENNELL CIR | 1535
0330 | FSU POLICE DEPARTMENT UNIT 2 | 330 PENNELL CIR | 2413
0331 | ALUMNI VL3 | 331 PENNELL CIR | 4950
0332 | ALUMNI VL3 | 332 PENNELL CIR | 1792
0333 | ALUMNI VL3 | 333 PENNELL CIR | 896
0334 | ALUMNI VL3 | 334 PENNELL CIR | 6600
0335 | ALUMNI VL3 | 335 PENNELL CIR | 4950
0336 | ALUMNI VL3 | 336 PENNELL CIR | 2688
0337 | ALUMNI VL3 | 337 PENNELL CIR | 1792
0338 | ALUMNI VL3 | 338 PENNELL CIR | 1792
0339 | ALUMNI VL3 | 339 PENNELL CIR | 4950
0340 | ALUMNI VL3 | 340 PENNELL CIR | 1792
0341 | ALUMNI VL3 | 341 PENNELL CIR | 4950
0342 | ALUMNI VL3 | 342 PENNELL CIR | 2688
0343 | ALUMNI VL3 | 343 PENNELL CIR | 4370
0344 | ALUMNI VL3 | 344 PENNELL CIR | 4370
0345 | ALUMNI VL3 | 345 PENNELL CIR | 3584
0346 | ALUMNI VL3 | 346 PENNELL CIR | 3584
0347 | ALUMNI VL3 | 347 PENNELL CIR | 6600
0348 | ALUMNI VL3 | 348 PENNELL CIR | 1792
0349 | ALUMNI VL3 | 349 PENNELL CIR | 2688
0350 | ALUMNI VL3 | 350 PENNELL CIR | 3584
0351 | ALUMNI VL3 | 351 PENNELL CIR | 4950
0352 | ALUMNI VL3 | 352 PENNELL CIR | 2688
0353 | ALUMNI VL3 | 353 PENNELL CIR | 6600
0354 | ALUMNI VL3 | 354 PENNELL CIR | 1792
0355 | ALUMNI VL3 | 355 PENNELL CIR | 6600
0356 | ALUMNI VL3 | 356 PENNELL CIR | 6600
0357 | ALUMNI VL3 | 357 PENNELL CIR | 1792
0358 | ALUMNI VL3 | 358 PENNELL CIR | 896
0359 | ALUMNI VL3 | 359 PENNELL CIR | 1792
0361 | FARM - ROOFING MATERIAL STORAGE | 1907 UNIVERSITY FARM RD | 1074
0363 | NURSERY - GROUNDS STORAGE | LEVY AVENUE | 3721
0364 | NURSERY - SCREENED GREENHOUSE | 1800 WEST ORANGE AVE | 1701
0365 | NURSERY - PLANT STORAGE | 1800 WEST ORANGE AVE | 2640
0366 | MISSION ROAD - GREENHOUSE | 2606 MISSION RD | 5320
0367 | MISSION ROAD - MAIN HOUSE | 2606 MISSION RD | 7232
0368 | NURSERY - WIRESHED STORAGE | 1800 WEST ORANGE AVE | 169
0368 | MISSION ROAD - POLE BARN | 2606 MISSION ROAD
0369 | NURSERY CARPORT | 1800 ORANGE AVE | 100
0369 | BLDG NO IS PREVIOUSLY IN SYSTEM | 2606 MISSION ROAD | 1150
0370 | WAREHOUSE - WEATHERLY FACILITY | 1799 ROBERTS AVE | 4080
0371 | NURSERY - CARPORT | 1800 WEST ORANGE AVE | 370
0373 | GOLF COURSE - PRACTICE LAB | 2530 POTTSDAMER ST | 1884
0375 | BUS STOP - ACADEMIC WAY | 825 ACADEMIC WAY | 271
0376 | CIRCUS HUT TICKET BOOTH | 147 CHIEFTAN WAY | 55
0377 | U.C. PARKING TOLL BOOTH | 289 CHAMPIONS WAY | 126
0378 | PARKING GARAGE #2 - TRADITIONS WAY | 860 TRADITIONS WAY | 236577
0379 | STUDENT SERVICES BUILDING | 874 TRADITIONS WAY | 51130
0380 | NORTHWEST REGIONAL DATA CENTER (NWRDC) | 2048 EAST PAUL DIRAC DR | 23952
0382 | NURSERY - BLDG 1 - OFFICE | 1800 WEST ORANGE AVE | 400
0383 | NURSERY - BLDG 2 - PURPLE | 1800 WEST ORANGE AVE | 116
0384 | NURSERY - BLDG 3 - FERTILIZER STORAGE | 1800 WEST ORANGE AVE | 66
0385 | STILES-SMITH TEAM BUILDING | 1119 SPIRIT WAY | 18184
0386 | SOCCER/SOFTBALL CONCESSIONS | 1119 SPIRIT WAY | 794
0387 | SOCCER/SOFTBALL RESTROOMS | 1119 SPIRIT WAY | 1012
0388 | SOCCER/SOFTBALL TICKET & SECURITY BUILDING | 1119 SPIRIT WAY | 348
0389 | SOFTBALL BATTING CAGE | 1119 SPIRT WAY | 14469
0390 | SOCCER PRESSBOX/SEATS | 1119 SPIRIT WAY | 777
0391 | SOFTBALL PRESSBOX & SEATING | 1119 SPIRIT WAY | 776
0392 | SOFTBALL HOME DUGOUT | 1119 SPIRIT WAY | 448
0393 | SOFTBALL VISITORS DUGOUT | 1119 SPIRIT WAY | 448
0394 | STAVROS CENTER | 250 S WOODWARD AVE | 5526
0395 | NURSERY - BLDG 4 - EQUIPMENT STORAGE | 1800 WEST ORANGE AVE | 100
0398 | APPLETON MUSEUM UTILITIES ADD. | SILVER SPRINGS BLVD. | 1178
0399 | APPLETON MUSEUM ADDITION | SILVER SPRINGS BLVD. | 25000
0400 | MARINE LAB- STORAGE(S.W.PARTS) | 3618 COASTAL HIGHWAY 98 | 80
0401 | MARINE LAB- STORAGE (LIVINGSTON) | 3618 COASTAL HIGHWAY 98 | 80
0402 | MARINE LAB- GEAR STORAGE | 3618 COASTAL HIGHWAY 98 | 306
0403 | MARINE LAB- OFFICE TRAILER | 3618 COASTAL HIGHWAY 98 | 672
0405 | MARINE LAB- DORM 5 | 3618 COASTAL HIGHWAY 98 | 2176
0406 | MARINE LAB- SHOP- DIVE PROGRAM | 3618 COASTAL HIGHWAY 98 | 2396
0407 | MARINE LAB- CLASSROOM - LAB | 3618 COASTAL HIGHWAY 98 | 2416
0408 | MARINE LAB- MAIN LAB BUILDING | 3618 COASTAL HIGHWAY 98 | 8573
0409 | MARINE LAB- DORM 1 AND 2 | 3618 COASTAL HIGHWAY 98 | 1088
0410 | MARINE LAB- DORM 4 AND 5 | 3618 COASTAL HIGHWAY 98 | 750
0411 | MARINE LAB- WELL HOUSE | 3618 COASTAL HIGHWAY 98 | 101
0412 | MARINE LAB- GENERATOR BUILDING | 3618 COASTAL HIGHWAY 98 | 216
0413 | MARINE LAB- PAINT STORAGE | 3618 COASTAL HIGHWAY 98 | 112
0414 | MARINE LAB- GREENHOUSE #1 | 3618 COASTAL HIGHWAY 98 | 1152
0415 | MARINE LAB- GREENHOUSE #2 | 3618 COASTAL HIGHWAY 98 | 576
0416 | MARINE LAB- CARETAKERS RESIDENCE | 3618 COASTAL HIGHWAY 98 | 768
0417 | MARINE LAB- GENERAL STORAGE | 3618 COASTAL HIGHWAY 98 | 360
0419 | MARINE LAB- STORAGE (LIVINGSTON) | 3618 COASTAL HIGHWAY 98 | 200
0420 | MARINE LAB- MOBILE WET LAB | 3618 COASTAL HIGHWAY 98 | 352
0425 | 930 W JEFFERSON ST | 930 W JEFFERSON ST
0426 | MARINE LAB MODULAR #1 | 323 W STADIUM DR
0427 | MARINE LAB MODULAR #2 | 323 W STADIUM D
0428 | MARINE LAB MODULAR #3 | 323 W STADIUM DR
0429 | MARINE LAB MODULAR #4 | 323 W STADIUM DR
0430 | MARINE LAB MODULAR #5 | 323 W STADIUM DR
0431 | MENDENHALL MAINTENANCE ANNEX | 961 LEARNING WAY | 1178
0432 | MARINE LAB MODULAR #6 | 323 W STADIUM DR
0433 | BLACK STUDENT UNION | 206 S WOODWARD AVE | 2124
0434 | NURSERY - OFFICE - TRAILER | 1800 WEST ORANGE AVE | 708
0435 | BUS STOP - CHIEFTAN WAY | 97 CHIEFTAN WAY | 271
0436 | THEATRE (FINE ARTS) ANNEX | 602 W CALL ST | 15805
0437 | E.A.P. FACILITY | 937 W JEFFERSON ST | 3382
0438 | ART TEACHING LABS | 525 W CALL ST | 6675
0439 | GUNTER (STATE GEOLOGY BLDG) - NUMBER ASSIGNED BY MAINT. | COLLEGE & COPELAND
0440 | PRESIDENT'S CART STORAGE | 140 UNIVERSITY WAY | 80
0441 | MARINE LAB- GREENHOUSE NORTH | 3618 COASTAL HIGHWAY 98 | 1248
0442 | MARINE LAB- GREENHOUSE SOUTH | 3618 COASTAL HIGHWAY 98 | 1248
0443 | MARRIAGE AND FAMILY CLINIC | 540 W JEFFERSON ST | 2362
0445 | SEMINOLE DINING SERVICES | 945 W JEFFERSON ST | 3383
0449 | ETV TRANSMITTER BUILDING 2 | 6559 SMITH CREEK RD | 1869
0450 | RINGLING- CENTER FOR THE PERFORMING ARTS | 5555 N TAMIAMI TRAIL | 105359
0454 | LIBRARY TECHNICAL SERVICES | 715 W MADISON ST | 14575
0455 | LIBRARY TECH STACKS | 713 W MADISON ST | 8725
0456 | HOWSER TICKET & CONCESSION | 270 CHIEFTAN WAY | 3177
0457 | HOWSER BATTING TUNNEL | 270 CHIEFTAN WAY | 9399
0458 | HOWSER GROUNDS MAINTENANCE | 270 CHIEFTAN WAY | 1492
0459 | HOWSER NORTH GATE | 270 CHIEFTAN WAY | 265
0460 | SCENIC STUDIO FACILITY | 619 S WOODWARD ST | 17916
0461 | MADISON STREET GARAGE - RECYCLING | 820 W MADISON ST | 3772
0462 | ALUMNI ASSO. MODULAR | 1030 WEST TENNESSEE | 5700
0462 | MARINE LAB- ADMIN BUILDING | 3618 COASTAL HIGHWAY 98 | 5681
0463 | PSYCHOLOGY MOBILE UNIT | COLLEGE & COPELAND | 162
0464 | MARINE LAB- MOBILE UNIT | 3618 COASTAL HIGHWAY 98 | 162
0465 | ALUMNI CENTER FACILITY | 1028 W TENNESSEE ST | 20940
0466 | CRITCHFIELD HALL (RECORDING) | 387 COMMERCE BLVD | 14031
0467 | FDLE MAIL FACILITY | 813B LAKE BRADFORD RD | 11152
0468 | CAMPUS SERVICES BLDG. | 609 W ST. AUGUSTINE ST | 3374
0469 | POSTAL AND RECEIVING | 800 W MADISON ST | 14532
0470 | THE LAB - BUILDING A | 502 S COPELAND ST | 5871
0471 | THE LAB - BUILDING B | 502 S COPELAND ST | 2914
0472 | THE LAB - BUILDING C | 502 S COPELAND ST | 88
0473 | PSYCHOLOGY MOBILE UNIT | COLLEGE & COPELAND | 162
0474 | PSYCHOLOGY MOBILE UNIT | COLLEGE & COPELAND | 162
0475 | METEOROLOGY MOBILE LAB | COLLEGE & COPELAND | 60
0476 | STATE STORAGE WAREHOUSE | 813A LK. BRADFORD RD | 16872
0477 | GAZEBO AT PRESIDENTS PARK | 449 FLORIDA WAY | 256
0478 | MASTER CRAFTSMAN STUDIO | 905 W GAINES ST | 5393
0480 | OLD MOTOR POOL GAS PUMPS COVER | 813B LK. BRADFORD RD | 1036
0485 | BUS STOP - STADIUM DR | 323 STADIUM DR | 962
0486 | M.L.TRACK RESTROOMS | 1104 SPIRIT WAY | 1852
0487 | CAR WASH - 1321 LK.BRADFORD | 1321 LAKE BRADFORD | 2018
0488 | SEMINOLE CAFE RESTURANT | 1110 W CALL ST | 19055
0490 | WAREHOUSE 3 -- LABOR & CONSTRUCTION | 813C LAKE BRADFORD RD | 13452
0491 | WAREHOUSE 4 - PARKING SERVICES | 813 LK. BRADFORD RD | 8280
0492 | WAREHOUSE - BUSINESS SERVICES | 1797 ROBERTS AVE | 8055
0493 | WAREHOUSE - SURPLUS | 1795 ROBERTS AVE | 6356
0494 | RIDGEWAY BUILDING | 715 W GAINES ST | 4972
0495 | RAGANS HALL 1 (A) | 923 LEARNING WAY | 52515
0496 | RAGANS HALL 2 (B) | 921 LEARNING WAY | 50362
0497 | RAGANS HALL 3 (C) | 930 W JEFFERSON ST | 51462
0498 | RAGANS HALL 4 (D) | 916 W JEFFERSON ST | 52512
0499 | HERITAGE TOWER | 272 CHIEFTAN WAY | 4
0500 | FLORIDA CAPITOL BUILDING | 400 S MONROE ST
0502 | LOS ALAMOS NATL LAB BLDG #127 | BLDG #127, MPA-CMMS/NHMFL TA35
0503 | THE KNOTT BUILDING | 601 S. DUVAL ST.
0522 | LEON COUNTY PUBLIC LIBRARY
0525 | SOUTH BRONOUGH - CRIMINOLOGY | S BRONOUGH
0527 | FAMU-FSU ENGINEERING BLDG. B | 2525 POTTSDAMER ST | 99755
0543 | WOODCREST OFFICE PARK | JOHN KNOX ROAD
0544 | TALLAHASSEE COMMUNITY COLLEGE (TCC) | PENSACOLA & APPLEYARD
0546 | ****DO NOT USE **** NEW 4546*** CIVIC CENTER - TURNER / TALL.-LEON CNTY | 505 W PENSACOLA ST
0565 | SUPREME COURT BUILDING | 500 S DUVAL ST
0577 | FAMU-FSU ENGINEERING BLDG. A | 2525 POTTSDAMER ST | 126641
0582 | FRINK TV TOWER | 12859 SW STATE RD 73 | 749
0585 | TURLINGTON BUILDING | 325 W GAINES ST
0586 | CHANNEL-6 TV TOWER | 30 RODDENBERRY RD | 3
0588 | FLORIDA A&M UNIVERSITY
0592 | FERMI NATIONAL ACCELERATOR LABORATORY | KIRD RD AND PINE ST
0596 | CERN | ESPL. DES PARTICULES 1
0603 | CITY WATER TOWER | 215 W JEFFERSON ST | 0
0605 | WOYS STATION | 29 BEGONIA ST
0606 | CHILDREN'S MEDICAL SERVICES | 5192 BAYOU BLVD
0610 | CITY WATER TANK | LONG AVE & 11TH ST
0613 | CITY WATER TANK - CARRABELLE | AVENUE D AND W 3RD ST
0615 | NORTHWOOD MALL | 1940 N MONROE ST | 10821
0617 | INDIAN RIVER COMMUNITY COLLEGE | 3209 VIRGINIA AVE
0618 | MCKENNON HALL/DAYTONA BEACH CC | 1200 W INTERNATIONAL SPEEDWAY BLVD
0621 | COLLEGE OF MEDICINE - JACKSON HOSPITAL | 4250 HOSPITAL DR
0622 | B. ALLEN RESIDENCE | 8708 SALAMANCA CT
0625 | CIRCUS TENT | 269 CHIEFTAIN WAY | 19263
0626 | FAMU/FSU COE INDUSTRIAL ENG. | 110 HAMILTON PARK DR.
0627 | TALLAHASSEE MEMORIAL HOSPITAL | 1300 MICCOSUKEE RD
0627 | GUNTER RESIDENCE | 505 SPRINGACRES COVE
0634 | ATLANTA DATA & DISASTER RECOVERY CTR. | 375 RIVERSIDE PKWY
0634 | WMBB-TV TOWER | 13735 SCOTTS FERRY RD
0635 | WMBB-TV TOWER | 13735 SCOTTS FERRY RD
0636 | ARTS AND SCIENCES FACULTY OFFICE | 4500 MONTVIEW BLVD
0640 | LOS ALAMOS NATL LAB BLDG# 124 | BLDG# 124, MPA-CMMS/NHMFL TA35
0641 | LOS ALAMOS NATL LAB BLDG# 125 | BLDG# 125, MPA-CMMS/NHMFL TA35
0642 | LOS ALAMOS NATL LAB BLDG# 126 | BLDG# 126, MPA-CMMS/NHMFL TA35
0643 | LOS ALAMOS NATL LAB BLDG# 294 | BLDG# 294, MPA-CMMS/NHMFL TA35
0644 | LOS ALAMOS NATL LAB BLDG# 301 | BLDG# 301, MPA-CMMS/NHMFL TA35
0650 | ST. ANDREWS MARINA | 3151 W 10TH ST
0651 | RICH RESIDENCE | 2204 AVALON DR
0652 | ALFERMANN RESIDENCE | 1198 PEEBLES DR
0653 | CHILDS RESIDENCE | 18268 MINOREA LN
0654 | MANN RESIDENCE | 6621 VALLEYPARK DR
0655 | MARIS (ATMA) RESIDENCE | 2571 MAPLELOFT LN
0656 | EDGAR RESIDENCE | 2870 CARRINGTON LAKES BLVD
0660 | GOODWILL OF SOUTHWESTERN PENNSYLVANIA | 2400 E CARSON ST
0661 | THE PLANTORY | 501 W 6TH ST
0662 | UNLOCKING DOORS | 12225 GREENVILLE AVE
0663 | CITY RESCUE MISSION | 426 S MCDUFF AVE
0664 | STATE EMERGENCY OPERATIONS CENTER | 2555 SHUMARD OAK BLVD
0665 | COLLEGE OF MEDICINE - LEE HEALTH | 2780 CLEVELAND AVE
0667 | COLLEGE OF MEDICINE - DERMATOLOGY ASSO. OF TALLAHASSEE - BUILDING A | 1707 RIGGINS RD
0668 | COLLEGE OF MEDICINE - DERMATOLOGY ASSO. OF TALLAHASSEE - BUILDING E | 1707 RIGGINS RD
0669 | COLLEGE OF MEDICINE - WINTER HAVEN HOSPITAL | 1201 1ST SOUTH
0670 | REID RESIDENCE | 320 SPRING RIDGE DR
0671 | WATKINS RESIDENCE | 428 CROSSWALK RD
0672 | CAWLEY RESIDENCE | 6 FERNS CT
0673 | IERNA RESIDENCE | 7801 POINT MEADOWS DR
0674 | COTTER RESIDENCE | 1601 MARINA ISLE WAY
0675 | OBRIEN RESIDENCE | 3401 N LAKEVIEW DR
0676 | ALI RESIDENCE | 12357 COLONY PRESERVE DR
0801 | OVERSEAS PROG. - FLORENCE ITALY | BORGO SS APOSTOLI | 1000
0802 | OVERSEAS PROG. - LONDON ENGLAND | 99 GREAT RUSSEL STREET, GREATER LONDON | 58309
0803 | CITY OF KNOWLEDGE | BUILDING #104 | 11304
0804 | FUQUA RESEARCH COMPLEX - SLIGER BUILDING | 2035 EAST PAUL DIRAC DR | 40521
0805 | FUQUA RESEARCH COMPLEX - MORGAN BUILDING | 2035 EAST PAUL DIRAC DRIVE | 36498
0806 | OVERSEAS PROG. - SWITZERLAND | EUROPE | 1000
0807 | OVERSEAS PROG. - COSTA RICA | CENTRAL AMERICA | 1000
0808 | NURSING - TALLAHASSEE MEMORIAL HOSPITAL | 1401 CENTERVILLE RD | 1000
0809 | NURSING - NON-TALLAHASSEE MEMORIAL HOSPITAL | 1401 CENTERVILLE RD | 1000
0811 | GUNTER (STATE GEOLOGY BLDG) | 903 W TENNESSEE ST | 20605
0813 | FUQUA RESEARCH COMPLEX - JOHNSON BUILDING | 2035 EAST PAUL DIRAC DR | 41807
0814 | FRANK SHAW BUILDING - INNOVATION PARK | 2031 EAST PAUL DIRAC DR | 42111
0815 | OVERSEAS PROG. - VIETNAM |  | 1000
0816 | OVERSEAS PROG. - RUSSIA | ASIA | 1000
0817 | P.C.- STUDENT GOV. CENTER ANNEX | 4750 COLLEGIATE DR.
0818 | P.C.- FACULTY ANNEX A | 4750 COLLEGIATE DR.
0819 | BASKETBALL TRAINING FACILITY | 520 W MADISON ST | 55995
0820 | VALENCIA CENTER | 2 CALLER BLANQUERIAS | 1000
0824 | RESEARCH FOUNDATION - BLDG. A | 2000 LEVY AVE | 84331
0825 | RESEARCH FOUNDATION - BLDG. B | 2010 LEVY AVE | 85280
0826 | CAPS DIELECTRICS LAB | 2000 LEVY AVE | 1215
0827 | CAPS MEDIUM VOLTAGE LAB | 2000 LEVY AVE | 3721
0828 | CAPS HIGH BAY LAB 2 | 2000 LEVY AVENUE | 26703
0830 | HYDROGEN RESEARCH FACILITY | E PAUL DIRAC DR
0831 | GCCC - ACADEMIC FACILITIES | COLLEGIATE DRIVE
0832 | CENTENNIAL BUILDING | DIRAC DRIVE
0833 | VARSITY PLAZA 1857 | 1857-B W. TENNESSEE ST. | 1593
0835 | NEIGHBORHOOD HEALTH SERVICES | 438 WEST BREVARD
0849 | CAPS HIGH-BAY LAB | 2000 LEVY AVE | 5215
0854 | MATERIALS RESEARCH BUILDING | 2005 LEVY AVE | 50238
0855 | AME BUILDING | 2003 LEVY AVE | 61726
0856 | AME UTILITIES BUILDING | 2003 LEVY AVE | 5165
0857 | AME STORAGE BUILDING - NOT CONSTRUCTED | 2003 LEVY AVE | 240
0860 | TECHNOLOGY SERVICES BUILDING | 1721 W PAUL DIRAC DR | 80234
0869 | SHORT STAY FACILITY | 1800 E. DIRAC DRIVE
0870 | IRCB | 2001 LEVY AVE | 125334
0870 | INTERDISCIPLINARY RESEARCH & COMMERCIALIZATION BUILDING | 2001 LEVY AVE | 125334
0900 | LEASE - 92-01 - APPLETON MUSEUM | SILVER SPRINGS BLVD.
0901 | APPLETON - MECHANICAL (#92-01) | SILVER SPRINGS BLVD.
0902 | APPLETON - WORKSHOP (#92-01) | SILVER SPRINGS BLVD.
0903 | LEASE - LSI | 4820-B KERRY FOREST PKWY | 1153
0927 | LEASE 1994:101-MFA (APPLEYARD) | 568 APPLEYARD
0928 | LEASE 1994:105-BFA (RAILROAD SQ) | RAILROAD SQ
0929 | 1994:105-BFA DK RM (RR SQ.) | RAILROAD SQ
0932 | CENTER FOR PREVENTION & EARLY INTERVENTION | 1331 E LAFAYETTE ST
0934 | LEASE 1995:110-TEACH&LEARN (CROSS CK) | 1353 CROSS CREEK CIR A&B
0937 | THEATER PROP STORAGE | 1119 W GAINES ST | 8875
0940 | LEASE 1996:108-CONFLICT RESOLUTION (IP-SHAW) | DIRAC DRIVE
0941 | LEASE 1998:102 - MAGLAB DUPLX | HONEYSUCKLE WAY
0945 | STADIUM PLACE - TRAINING CENTER | 493 STADIUM DR | 11000
0948 | LEASE 2003:110 - FILM SCHOOL | 607 MCDONNELL DRIVE
0949 | LEASE 2000:101-MAGLAB APTS (JEFFERSON POINT) | THARPE ST
0950 | HUMAN RIGHTS CENTER | 426 W JEFFERSON ST
0952 | VARSITY PLAZA 1847 | 1847 W TENNESSEE ST | 13943
0953 | 2011:101-AUTISM CTR. | SUITE 72,65,&33 1940 N MONROE ST | 10821
0954 | LEASE 2000:106-HEALTHY BABY(QUINCY) | JEFFERSON ST
0956 | LEASE 2000:108 -TOBACCO CTR (STORAGE) | DIRAC DR
0957 | LEASE 2000:109-HLTH/HMN (IP-MORGAN236) | DIRAC DR
0960 | LEASE - FSU FOUNDATION | 1035 COMMERCIAL DRIVE
0961 | LEASE 2001:101-SARASOTA(FA OFFICES) | STORAGE RD
0963 | LEASE - 2011:111 - FL NATURAL AREAS INVENTORY - 148000 | 1018 THOMASVILLE RD, SUITE 112
0966 | LEASE - 2001:106-RINGLING STORAGE | STORAGE RD
0967 | 2001:107-HLTH EQUITY(355B MONR | 355 N MONROE ST B
0968 | 2001:108-LSI PTC(7200 CITY CTR) | 227 N BRONOUGH ST
0971 | 2002:101-COAPS (IP-JOHNSON) | DIRAC DR
0972 | 2002:102-EARTH SRF CTR(IP-SHAW | DIRAC DR
0973 | 2002:103-READ RSH(7250 CC) | BROUGHT ST
0974 | CENTER FOR PREVENTION & EARLY INTERVENTION | 1331 E LAYFAYETTE SUITE F
0975 | LEASE - 2007:106 - FLORIDA INCLUSION NETWORK | 355B N MONROE ST
0976 | 2002:106-POP.STUDY(MIAMI)
0977 | 2002:107-ERP OFF.(IP-SHAW) | DIRAC DR
0978 | CENTER FOR PREVENTION & EARLY INTERVENTION | 385 E JEFFERSON ST
0979 | LEASE - 2008:102 - COM ORLANDO | 250 E COLONIAL DR, SUITE 200
0980 | 2002:110-COM (PENSACOLA) | UNIVERSITY PKWY
0981 | 2002:111-CBTR/IICER(IP-MORGAN) | DIRAC DR
0982 | 2002:112-CBTR/IICER(IP-MORGAN) | DIRAC DR
0983 | 2002:113-CBTR/IICER(IP-MORGAN) | DIRAC DR
0984 | 2002:115-LSI-READ.RSH(7600 CC) | BROUGHT ST
0985 | LEASE - 2009:107 - FLORIDA CAMPUS COMP | 1801 MICCOSUKEE COMMONS
0986 | 2011:108-INST GOV | 3200 COMMONWEALTH BLVD
0987 | 2002:118-HEALTY EQUITY(QUINCY) | 385 W JEFFERSON ST D
0988 | LEASE - 2002:119 - COM TALLAHASSEE | 3331 CAPITAL OAKS DR
0989 | 2006:114-LSI READING RESEARCH | 227 N BRONOUGH ST SUITE 4050
0990 | 2003:101-BEACHS&SHORES (IP) | DIRAC DR
0991 | 2003:102-EDUC.SERV.PROG.(IP) | DIRAC DR
0992 | 2003:103-ED.SERV.PROG (IP) | DIRAC DR
0993 | C.O.M. PENSACOLA | 8880 UNIVERSITY PARKWAY SUITE A
0994 | 2003:105-JJEEP WOODCREST | JOHN KNOX RD
0995 | 2003:106-TOBACCO CTR.(IP) | DIRAC DR
0996 | 2003:111-LSI 2ND FL. | 227 N. BRONOUGH ST
0997 | 2003:112 - LSI 4TH FL. | 227 N. BRONOUGH ST
0998 | 2003:114 - COM GAINESVILLE | 3615 SW 13TH STREET
1001 | P.C.- QUAD 1 (MAINTENANCE) | 4750 COLLEGIATE DR. | 2512
1002 | P.C.- QUAD 2 (OFFICE) | 4917 N BAY DR | 2512
1003 | P.C.- QUAD 3 (OFFICE/CLASS) | 4915 TO 4919 BAY DR | 2512
1004 | PANAMA CITY - TRACTOR STORAGE | 4750 COLLEGIATE DR. | 238
1005 | PANAMA CITY - BARRON BUILDING | 4750 COLLEGIATE DR. | 39853
1006 | PANAMA CITY - OFFICE BUILDING (B NORTH) | 4750 COLLEGIATE DR. | 12526
1007 | PANAMA CITY - TECHNOLOGY BUILDING (B SOUTH) | 4750 COLLEGIATE DR. | 27256
1008 | PANAMA CITY - BAY BUILDING (BLDG. C) | 4750 COLLEGIATE DR. | 14456
1009 | PANAMA CITY - AUDITORIUM | 4750 COLLEGIATE DR. | 6946
1010 | PANAMA CITY - WFSG-TV TRANSMITTER BUILDING | 11411 LANDFILL RD | 1600
1012 | PANAMA CITY - BLAND CONFERENCE CENTER | 4750 COLLEGIATE DR. | 4268
1013 | 4750 COLL. DR | 4750 COLLEGIATE DR | 2404
1014 | PANAMA CITY - ADMINISTRATIVE SERVICES CENTER | 4750 COLLEGIATE DR. | 19830
1015 | PANAMA CITY - HOLLEY ACADEMIC CENTER | 4750 COLLEGIATE DR. | 79548
1016 | LEASE - 2007:115 - AUTISM CENTER (PC) | 2611-A W 23RD ST
1017 | SEMINOLE LANDING | 5000 N BAY DR | 20000
2000 | CHALLENGER LEARNING CENTER | 200 S DUVAL ST | 39169
2001 | FSUS COMMUNITY STORE FRONT 1 | 3000 SCHOOL HOUSE ROAD | 10808
2002 | FSUS COMMUNITY STORE FRONT 2 | 3000 SCHOOL HOUSE ROAD | 10808
2003 | FSUS HIGH AND MIDDLE SCHOOL 3 | 3000 SCHOOL HOUSE ROAD | 37118
2004 | FSUS HIGH AND MIDDLE SCHOOL 4 | 3000 SCHOOL HOUSE ROAD | 37118
2005 | FSUS PRIMARY SCHOOL 5 | 3000 SCHOOL HOUSE ROAD | 14578
2006 | FSUS PRIMARY SCHOOL 6 | 3000 SCHOOL HOUSE ROAD | 16427
2007 | FSUS MEDIA CENTER 7 | 3000 SCHOOL HOUSE ROAD | 3716
2008 | FSUS GYMNASIUM 8 | 3000 SCHOOL HOUSE ROAD | 22980
2009 | FSUS AUDITORIA 9 | 3000 SCHOOL HOUSE ROAD | 23140
2010 | FSUS ADMINISTRATION 10 | 3000 SCHOOL HOUSE ROAD | 5661
2011 | FSUS PRIMARY AND ARTS BUILDING | 3000 SCHOOL HOUSE ROAD | 840
2012 | FSUS SCIENCE/INTERMEDIATE BLDG | 3000 SCHOOL HOUSE ROAD | 6180
2013 | FSUS PRIMARY & ELEMENTARY ART CLASSROOM | 3000 SCHOOL HOUSE ROAD | 11717
2020 | FSU FOUNDATION BUILDING | 325 W COLLEGE AVE | 28352
2021 | JIM MORAN BUILDING | 111 S MONROE ST | 24150
2022 | THE CLOCK BUILDING | 200 W COLLEGE AVE | 47162
2023 | PLAZA TOWER CONDOS - KLEMAN PLAZA | 300 S DUVAL ST | 20062
2030 | FSUS BASEBALL/SOFTBALL CONCESSIONS | 3000 SCHOOL HOUSE ROAD
2031 | FSUS HOME DUGOUT 1 | 3000 SCHOOL HOUSE ROAD
2032 | FSUS VISITOR DUGOUT 1 | 3000 SCHOOL HOUSE ROAD
2033 | FSUS BASEBALL/SOFTBALL PRESSBOX | 3000 SCHOOL HOUSE ROAD
2034 | FSUS BASEBALL POLE BARN/STORAGE | 3000 SCHOOL HOUSE ROAD
2035 | FSUS HOME DUGOUT 2 | 3000 SCHOOL HOUSE ROAD
2036 | FSUS VISITOR DUGOUT 2 | 3000 SCHOOL HOUSE ROAD
2037 | FSUS TRACK CONCESSION | 3000 SCHOOL HOUSE ROAD
2038 | FSUS TRACK RESTROOMS | 3000 SCHOOL HOUSE ROAD
2039 | FSUS TRACK PORTABLE | 3000 SCHOOL HOUSE ROAD
2040 | FSUS TRACK HOME BLEACHERS/PRESSBOX | 3000 SCHOOL HOUSE ROAD
2041 | FSUS TRACK STORAGE SHED | 3000 SCHOOL HOUSE ROAD
2042 | FSUS OPEN AIR STORAGE | 3000 SCHOOL HOUSE ROAD
2043 | FSUS STEAM BUILDING | 3000 SCHOOL HOUSE ROAD
2098 | FSUS PORTABLE #2 | 3000 SCHOOL HOUSE ROAD | 843
2099 | FSUS PORTABLE #1 | 3000 SCHOOL HOUSE ROAD | 843
2200 | MARINE LAB- FUEL PUMP CANOPY | 3618 COASTAL HIGHWAY 98 | 276
2201 | MARINE LAB- STORAGE - SATS | 3618 COASTAL HIGHWAY 98 | 61
2202 | MARINE LAB- CARPENTER SHOP | 3618 COASTAL HIGHWAY 98 | 413
2203 | MARINE LAB- STORAGE - FLAMMABLES | 3618 COASTAL HIGHWAY 98 | 112
2204 | MARINE LAB- STORAGE - FACILITIES | 3618 COASTAL HIGHWAY 98 | 193
2205 | MARINE LAB- STORAGE - MARINE OPS | 3618 COASTAL HIGHWAY 98 | 138
2206 | MARINE LAB- POTABLE WATER CHLORINATION COVERED AREA | 3618 COASTAL HIGHWAY 98 | 53
2207 | MARINE LAB- STORAGE STATS PROG | 3618 COASTAL HIGHWAY 98 | 61
2208 | MARINE LAB- SCIENTIFIC WATER WELL | 3618 COASTAL HIGHWAY 98 | 78
2209 | MARINE LAB- STORAGE - ZOOLOGICAL COLLECTION | 3618 COASTAL HIGHWAY 98 | 84
2210 | MARINE LAB- WALK-IN FREEZER 1 | 3618 COASTAL HIGHWAY 98 | 105
2211 | MARINE LAB- STORAGE - GRUBBS | 3618 COASTAL HIGHWAY 98 | 121
2212 | MARINE LAB- SEA WATER TOWER | 3618 COASTAL HIGHWAY 98 | 200
2213 | MARINE LAB- WALK-IN FREEZER 2 | 3618 COASTAL HIGHWAY 98 | 105
2214 | MARINE LAB- HERRNKIND GREENHOUSE | 3618 COASTAL HIGHWAY 98 | 900
2215 | MARINE LAB- STORAGE - FACULTY | 3618 COASTAL HIGHWAY 98 | 710
2216 | MARINE LAB- OPEN AIR CLASSROOM | 3618 COASTAL HIGHWAY 98 | 600
2217 | MARINE LAB- CONDITIONED STORAGE - FACULTY | 3618 COASTAL HIGHWAY 98 | 792
2218 | MARINE LAB- STORAGE - SEA WATER | 3618 COASTAL HIGHWAY 98 | 201
2219 | MARINE LAB- BOAT STORAGE | 3618 COASTAL HIGHWAY 98 | 2084
2220 | MARINE LAB- WET TABLE PAVILION | 3618 COASTAL HIGHWAY 98 | 369
2221 | MARINE LAB- | 3618 COASTAL HIGHWAY 98
2222 | MARINE LAB- BRIDGE HATCHERY GREENHOUSE | 3618 COASTAL HIGHWAY 98 | 1509
2223 | MARINE LAB- HATCHERY GREENHOUSE | 3618 COASTAL HIGHWAY 98 | 3120
2224 | MARINE LAB - STORAGE | 3618 HIGHWAY 98 | 160
2600 | COLLEGE OF MEDICINE - COLLIER CLINIC (IMMOKALEE) | 1441 HERITAGE BLVD. | 39817
3001 | HERITAGE GROVE BLDG 1 | 1900 HERITAGE GROVE CIR | 1000
3002 | HERITAGE GROVE BLDG 2 | 1904 HERITAGE GROVE CIR | 1000
3003 | HERITAGE GROVE BLDG 3 | 1908 HERITAGE GROVE CIR | 1000
3004 | HERITAGE GROVE BLDG 4 | 1912 HERITAGE GROVE CIR | 1000
3005 | HERITAGE GROVE BLDG 5 | 1916 HERITAGE GROVE CIR | 1000
3006 | HERITAGE GROVE BLDG 6 | 1920 HERITAGE GROVE CIR | 1000
3007 | HERITAGE GROVE BLDG 7 | 1924 HERITAGE GROVE CIR | 1000
3008 | HERITAGE GROVE BLDG 8 | 1936 HERITAGE GROVE CIR
3009 | HERITAGE GROVE BLDG 9 | 1940 HERITAGE GROVE CIR | 1000
3010 | HERITAGE GROVE BLDG 10 - HOBBS HALL | 1944 HERITAGE GROVE CIR | 23998
3011 | HERITAGE GROVE BLDG 11 | 1948 HERITAGE GROVE CIR
3012 | HERITAGE GROVE BLDG 12 | 1952 HERITAGE GROVE CIR
3013 | HERITAGE GROVE BLDG 13 | 1947 HERITAGE GROVE CIR
3014 | HERITAGE GROVE BLDG 14 | 1939 HERITAGE GROVE CIR
3110 | HERITAGE GROVE BLDG 10.5 - PEACOCK HALL | 1944 HERITAGE GROVE CIR | 15.266
3367 | MISSION ROAD - AVIARY | 2606 MISSION ROAD | 960
3368 | MISSION ROAD - POLE BARN | 2606 MISSION ROAD | 1326
3401 | COMMONWEALTH - RESEARCH'S ENTREPRENEURIAL BUILDING | 3000 COMMONWEALTH BLVD | 38823
3402 | COMMONWEALTH - RESEARCH COMPLEX | 3200 COMMONWEALTH BLVD | 19383
3403 | COMMONWEALTH - MARYLAND BUILDING | 2139 MARYLAND CIR | 33914
3801 | FACILITY FOR ARTS RESEARCH | 3216 SESSIONS ROAD | 26498
4000 | CAGE WASH FACILITY | 315 STADIUM DR | 11081
4001 | COLLEGE OF MEDICINE - THRASHER BUILDING | 1115 W CALL ST | 156631
4002 | COLLEGE OF MEDICINE - RESEARCH BUILDING | 1115 W CALL ST | 147789
4003 | COLLEGE OF MEDICINE - PEADEN AUDITORIUM | 1115 W CALL ST | 8164
4004 | PSYCHOLOGY DEPARTMENT BUILDING | 1107 W CALL ST | 179408
4005 | PSYCHOLOGY DEPARTMENT AUDITORIUM | 1107 W CALL ST | 7539
4006 | PARKING GARAGE #3 - SPIRIT WAY | 1122 SPIRIT WAY | 520885
4007 | KING LIFE SCIENCE BUILDING | 319 STADIUM DR | 181078
4008 | CHEMICAL SCIENCE LABORATORIES | 102 VARSITY WAY | 169308
4009 | CLASSROOM BUILDING (HCB) | 989 LEARNING WAY | 106533
4010 | EOAS BUILDING | 1011 ACADEMIC WAY | 143390
4011 | DUNLAP SUCCESS CENTER | 100 S WOODWARD AVE | 48914
4012 | PRESIDENT'S HOUSE | 1000 W TENNESSEE ST | 16092
4013 | SATELLITE UTILITIES PLANT 2 | 115 VARSITY WAY | 7921
4014 | PARKING GARAGE #4 - CALL ST | 504 W CALL ST | 295730
4016 | SPECIAL EVENTS STORAGE | 1000 W TENNESSEE ST | 1170
4018 | NEW STUDENT UNION | 75 N WOODWARD AVE | 260248
4020 | WILDWOOD HALLS 1 | 938 W JEFFERSON ST | 80257
4021 | WILDWOOD HALLS 2 | 202 VARSITY DR | 80105
4022 | TRADITIONS HALL | 945 LEARNING WAY | 125708
4023 | DEGRAFF HALL EAST | 808 W TENNESSEE ST | 85751
4024 | DEGRAFF HALL WEST | 810 W TENNESSEE ST | 84102
4025 | PARKING GARAGE #5 - ST AUGUSTINE ST | 501 S COPELAND ST | 279863
4026 | FOOD SERVICES FACILITY - NOT CONSTRUCTED | W CALL ST
4027 | ALPHA DELTA PI PAVILION | 713 UNIVERSITY WAY | 563
4028 | PARKING GARAGE #6 - W PENSACOLA ST | 410 WALKER ST | 332934
4029 | HONORS SCHOLARS & FELLOWS | 127 HONORS WAY | 40536
4030 | COBURN WELLNESS CENTER | 960 LEARNING WAY | 176828
4031 | THE GLOBE | 110 S WOODWARD AVE | 42434
4032 | WOODWARD & ST. AUGUSTINE STARBUCKS - NOT CONSTRUCTED | 505 S WOODWARD ST
4033 | CHILD DEVELOPMENT CENTER | 612 S COPELAND ST | 16514
4034 | BILL'S BOOKSTORE | 111 S COPELAND ST | 12005
4039 | VETERANS LEGACY CENTER | UNKNOWN
4040 | COLLEGE OF LAW - ADVOCACY CENTER | 301 S M L KING JR BLVD | 55018
4041 | WARREN BLDG. | 201 W BLOXHAM ST | 36969
4042 | WINCHESTER BLDG. | 305 BLOUNT ST | 21518
4042 | WINCHESTER BLDG.- CHANGED SITE | 305 BLOUNT ST | 21518
4043 | C.C. - BLOXHAM ANNEX A | 319 E GAINES ST | 6245
4044 | C.C. - BLOXHAM ANNEX B | 309 E GAINES ST | 5021
4045 | C.C. - BLOXHAM ANNEX C | 325 E GAINES ST | 4525
4046 | C.C. - FIRESTONE BLDG | 401 E GAINES ST | 43582
4047 | C.C. - FIRESTONE ANNEX | 401 E BLOXHAM ST | 21690
4048 | C.C. - FIRESTONE UTILITIES | 401 E GAINES ST | 420
4049 | C.C. - CHAPMAN BLDG | 813 S GADSDEN ST | 6934
4050 | C.C. - DOUGLAS BUILDING | 1005 S ML KING BLVD | 1104
4060 | DORMAN HALL | 101 S WOODWARD AVE | 109305
4061 | DEVINEY HALL | 111 S WOODWARD AVE | 105173
4062 | AZALEA HALL | 824 W JEFFERSON ST | 130196
4063 | MAGNOLIA HALL | 802 UNIVERSITY WAY | 112637
4070 | CHIEFTAN GREEN APARTMENTS | 319 CONRADI ST
4076 | TANNER EQUIPMENT SHED | 830 W JEFFERSON ST | 1474
4077 | MAINTENANCE GAS PUMPS | 969 LEARNING WAY | 900
4078 | MAINTENANCE SHED 1 | 965 LEARNING WAY | 780
4079 | MAINTENANCE SHED 2 | 965 LEARNING WAY | 832
4080 | MAINTENANCE SHED 3 | 965 LEARNING WAY | 1023
4088 | CIVIC CTR. BAT HOUSE | 505 W PENSACOLA ST | 15
4090 | DUNLAP PRACTICE FACILITY | 389 STADIUM DR | 96131
4091 | PRACTICE FIELDS TOWER | 389 STADIUM DR | 36
4092 | SAND VOLLEYBALL STORAGE BUILDING | 1110 SPIRIT WAY | 140
4093 | SAND VOLLEYBALL BUILDING | 1110 SPIRIT WAY
4094 | FOOTBALL OPERATIONS FACILITY | 391 STADIUM DRIVE | 150000
4095 | TRACK STORAGE FACILITY | 1104 SPIRIT WAY
4104 | PSYCHOLOGY-COLLEGE OF MEDICINE UTILITIES BUILDING | 1106 W CALL ST | 794
4114 | KEMPER LAB (OGZEB) | 1035 ATOMIC WAY | 2576
4115 | BASEBALL CAMERA TOWER | CHIEFTAN WAY
4117 | TENT TRAILER | 268 CHIEFTAN WAY | 425
4130 | GATE CONTROL BOOTH - WELLNESS CENTER | LEARNING WAY | 26
4190 | VENDING HUT - UNION | CALL PEDESTRIAN WAY AT UNION | 320
4191 | VENDING HUT - CHIEFTAN WAY | CHIEFTAN WAY AND CALL STREET | 173
4192 | VENDING HUT - SALLEY | CALL STREET | 734
4193 | KIOSK - MURPHREE & CALL | W CALL ST | 131
4223 | GARNET-N-GO | 284 CHAMPIONS WAY | 1806
4225 | BUS STOP - UNIVERSITY CENTER | 292 CHAMPIONS WAY | 942
4240 | WHITCOMB FACILITY (BAND) | 122 VARSITY WAY | 1347
4241 | CAMPUS GARDEN SHED | 211 VARSITY DR | 65
4242 | CAMPUS GARDEN PAVILION | 211 VARSITY DR | 551
4249 | ZONE 3 MAINTENANCE STORAGE | 1187 ACADEMIC WAY | 230
4255 | GREENE-LEWIS HOUSE | 535 W COLLEGE AVE | 3355
4385 | SOCCER STORAGE FACILITY | 1119 SPIRIT WAY | 120
4386 | SOCCER AND SOFTBALL STORAGE FACILITY | 1119 SPIRIT WAY | 120
4390 | SOCCER CAMERA TOWER | STADIUM DRIVE
4391 | SOFTBALL CAMERA TOWER | SPIRIT WAY
4392 | SOFTBALL SHADE STRUCTURE | 1119 SPIRIT WAY | 4673
4400 | PIMS - MODULAR UNIT 1 | W.CALL & STADIUM DR
4408 | PELLETIZER BUILDING - NOT CONSTRUCTED | 95 CHIEFTAN WAY
4433 | BLACK STUDENT UNION | 921 W JEFFERSON ST | 7248
4446 | WESTSIDE COURTS PAVILION | 1159 HULL DR. | 1574
4452 | CARNAGHI ARTS BUILDING B - NOT CONSTRUCTED | 2214 BELLE VUE WAY
4453 | CARNAGHI ARTS BUILDING C - NOT CONSTRUCTED | 2214 BELLE VUE WAY
4490 | LABOR AND CONSTRUCTION STORAGE | 813C LAKE BRADFORD RD | 676
4497 | CARNAGHI ARTS BUILDING A - NOT CONSTRUCTED | 2214 BELLE VUE WAY | 421
4498 | CARNAGHI ARTS BUILDING B | 2214 BELLE VUE WAY | 421
4499 | CARNAGHI ARTS BUILDING C - NOT CONSTRUCTED | 2214 BELLE VUE WAY | 192
4500 | CARNAGHI ARTS BUILDING | 2214 BELLE VUE WAY | 105560
4501 | RECYCLING CTR.- BLDG.1 | 1238 CRATE DR | 19555
4502 | RECYCLING CTR.- BLDG.2 | 1235 AIRPORT DR | 4682
4503 | RECYCLING CTR.- BLDG.3 | 1237 AIRPORT DR | 2551
4504 | RECYCLING CTR.- BLDG.4 | 1241 AIRPORT DR | 4150
4505 | FACILITIES WAREHOUSE | 1207 EPPES DR | 8671
4507 | ACADEMIC SUPPORT FACILITY | LAKE BRADFORD RD
4540 | LEGACY HALL (COLLEGE OF BUSINESS) | 402 W GAINES ST | 210000
4546 | TUCKER CIVIC CENTER | 505 W PENSACOLA ST | 487359
4551 | CARNAGHI ARTS BUILDING A | 2214 BELLE VUE WAY | 421
4552 | CARNAGHI ARTS BUILDING B | 2214 BELLE VUE WAY | 421
4553 | CARNAGHI ARTS BUILDING C | 2214 BELLE VUE WAY | 192
4901 | LEASE - 2008:101 - UNIT 1 | 805 W MADISON ST | 6325
4902 | LEASE - 2008:101 - UNIT 2 | 809 W MADISON ST | 32622
4903 | LEASE - 2008:101 - UNIT 3 | 811 W MADISON ST | 6804
4904 | LEASE - 2008:101 - UNIT 4 | 813 W MADISON ST | 3249
4905 | LEASE - 2008:101 - UNIT 5 | 815 W MADISON ST | 14125
4973 | FSU FOUNDATION APARTMENT BUILDING | 325 CONRADI ST
4974 | UPS STORE | 206 S WOODWARD AVE | 3928
4975 | CCF HOUSE 2 | 520 WEST COLLEGE
4976 | CCF HOUSE 1 | 522 WEST COLLEGE
4977 | CCF HOUSE | 524 WEST COLLEGE
4978 | SIGMA NU | 530 W COLLEGE
4979 | SIGMA NU OUTBUILDING | 530 W COLLEGE AVE
4980 | BUILDING 1 DEMOLITION. | 703 RAILROAD AVE | 11428
4981 | BUILDING 2 DEMOLITION. | 707 RAILROAD AVE | 11428
4982 | BUILDING 3 DEMOLITION. | 711 RAILROAD AVE | 11428
4983 | OLD HATTIES UPHOLSTERY | 703 RAILROAD AVE | 11428
4984 | BB BUILDING | 426 DUNWOODY ST | 2250
4985 | OSCEOLA DUPLEX - DUNWOODY | 402-404 DUNWOODY ST | 1888
4986 | PALM COURT | 537 PALM CT
4987 | PALM COURT | 541 PALM COURT
4988 | PALM COURT | 541A PALM CT
4989 | 547 PALM COURT | 547 PALM COURT
4990 | OLD KAPPA SIGMA HOUSE | 112 S WOODWARD
4991 | 921 W. JEFFERSON (KAPPA ALPHA) | 921 W. JEFFERSON ST
4992 | TKE HOUSE | 916 W COLLEGE AVE
4993 | 504 MURPHREE ST | 504 MURPHREE ST
4994 | 508 MURPHREE ST | 508 MURPHREE ST
4995 | 514 MURPHREE ST | 514 MURPHREE ST
4996 | 520 MURPHREE ST | 520 MURPHREE ST
4997 | 526 MURPHREE ST | 526 MURPHREE ST
4998 | FIJI HOUSE | 526 W PENSACOLA ST
5045 | ENGINEERING - SHED 1 | 2525 POTTSDAMER ST | 451
5405 | ENGINEERING - PORTABLE 405 | 2525 POTTSDAMER ST | 1789
5406 | ENGINEERING - PORTABLE 406 | 2525 POTTSDAMER ST | 987
5407 | ENGINEERING - PORTABLE 407 | 2525 POTTSDAMER ST | 1047
5408 | ENGINEERING - PORTABLE 408 | 2525 POTTSDAMER ST | 1557
5410 | ENGINEERING - PORTABLE 410 | 2525 POTTSDAMER ST
5411 | ENGINEERING - PORTABLE 411 | 2525 POTTSDAMER ST
5412 | ENGINEERING - PORTABLE 412 | 2525 POTTSDAMER ST
5414 | ENGINEERING - PORTABLE 414 | 2525 POTTSDAMER ST
5415 | ENGINEERING - PORTABLE 415 | 2525 POTTSDAMER ST
5416 | ENGINEERING - PORTABLE 416 | 2525 POTTSDAMER ST
5417 | ENGINEERING - PORTABLE 1 | 2525 POTTSDAMER ST | 280
5418 | ENGINEERING - PORTABLE 2 | 2525 POTTSDAMER ST | 200
5420 | ENGINEERING - MATERIALS STORAGE | 2525 POTTSDAMER ST | 305
6000 | WESTVIEW PLAZA I | SUITE 211, WESTVIEW PLAZA I
6001 | COLLEGE OF MEDICINE - OB-GYN CLINIC | 5045 CARPENTER CREEK DRIVE | 1000
6002 | SUCCESS LANE BUILDING | 4371 SUCCESS LN
6003 | SEMORAN BLVD BUILDING | 5449 S SEMORAN BLVD
6004 | COLLEGE BLVD BUILDING | 100 COLLEGE BLVD
6005 | GABLES EXECUTIVE OFFICES (2010:102 - LSI) | 2655 LEJEUNE RD
6006 | CITY CENTRE BUILDING (2009:104 FCPM) | 227 N BRONOUGH ST
6007 | LIBERTY SQUARE BUILDING (2020:103 - CTR. AUTISM , CARD) | 2611-A W 23RD ST
6008 | COM - ORLANDO REGIONAL MEDICAL FACILITY (2020:107) | 250 E COLONIAL DR
6009 | BAYOU BLVD BUILDING | 5154 BAYOU BLVD
6010 | COLLEGE OF MEDICINE - SARASOTA REGIONAL MEDICAL FACILITY | 201 COCOANUT AVE
6010 | CONSTANT FRIENDSHIP BLVD. BLDG | 410 CONSTANT FRIENDSHIP BLVD.
6011 | WEST BLVD BUILDING | 753 WEST BLVD
6012 | CAPITOL STREET BUILDING | 400/444 N CAPITOL ST NW
6013 | SAMPLE ROAD BUILDING | 10191 W SAMPLE RD
6014 | MARYWEATHER LANE BUILDING | 3807 MARYWEATHER LN
6015 | BROGAN MUSEUM | 300 W PENSACOLA ST
6016 | WESTSIDE MINI STORAGE | 106 BLOUNTSTOWN HWY
6017 | WHISPERING WOODS CENTER BLDG 2 | 7451 WILES RD
6018 | OAKLAND COMMERCE CENTER | 3411 N POWERLINE RD
6019 | LEASE - REQUEST 10022 - LSI - 186000 | 8800 133RD AVE N | 1470
6020 | COM - AUTISM INSTITUTE (2016:105) | 2312 KILLEARN CENTER BLVD | 20000
6021 | AUTISM INSTITUTE | 2311 KILLEARN CENTER BLVD
6022 | COM - PENSACOLA REGIONAL MEDICAL FACILITY (UWF BLDG) | 1000 UNIVERSITY PARKWAY | 4324
6023 | COB - JIM MORAN INSTITUTE (2016:101) | 1401 E BROWARD BLVD | 2083
6024 | GOODLETTE ROAD BUILDING | 671 GOODLETTE RD N STE 140
6025 | ARLINGTON BUILDING (2016:110 - SOCIAL WORK) | 5920 ARLINGTON EXPRESSWAY
6026 | COLLEGE ROAD BUILDING | 3001 SW COLLEGE RD
6027 | HAUSER RESIDENCE | 12242 OLIVE JONES ROAD
6028 | SCHMEE RESIDENCE | 255 EVERNIA ST
6029 | CARBALLO-FLORES RESIDENCE | 11328 ASHBORO DR
6030 | LAFAYETTE BUILDING 1339 (1996:102 - CPEI) | 1339 E LAFAYETTE ST
6031 | LAFAYETTE BUILDING 1331 (2015:108 - CPEI) | 1331 E LAFAYETTE ST
6033 | TALLAHASSEE REGIONAL MEDICAL SCHOOL CAMPUS | 3331 CAPITAL OAKS DR
6034 | MONTICELLO SQUARE (2011:111 - FANI) | 1018 THOMASVILLE RD, SUITE 112
6035 | KERRY FOREST PKWY BUILDING | 4820-B KERRY FOREST PKWY | 1153
6036 | MICCOSUKEE COMMONS | 1801 MICCOSUKEE COMMONS
6037 | QUINCY CENTER | 385 E JEFFERSON ST | 6343
6038 | DIXIE DRIVE BUILDING | 5625 DIXIE DRIVE
6039 | COMMERCIAL DRIVE BUILDING | 1035 COMMERCIAL DRIVE
6040 | QUADRANT 1 (2017:104 - JMI) | 4651 SALISBURY ROAD
6040 | RINGLING TALLEVAST WAREHOUSE | 500 TALLEVAST ROAD
6040 | LEASE# 2019:104 | 2911 ROBERTS AVE | 613
6041 | ALUMNI CENTER SIGN (2013:500 - CITY R-O-W) | W TENNESSEE ST
6042 | TALLEVAST WAREHOUSE (2019:113 - RINGLING WHRS) | 500 TALLEVAST ROAD
6043 | AUTISM INSTITUTE TANIC DR BLDG 1 | 26837 TANIC DRIVE
6044 | AUTISM INSTITUTE TANIC DR BLDG 2 | 4302 HENDERSON BLVD
6045 | PARKING DECK (2018:105 - FSU FOUNDATION) | 209 EAST PARK AVENUE
6046 | COMMONWEALTH STORAGE FACILITIES (2010:115 - MAG LAB) | 1531 COMMONWEALTH BUSINESS DR
6047 | COM - FT. PIERCE REGIONAL MEDICAL FACILITY (2006:900) | 2498 S 35TH ST | 9264
6048 | COM - DAYTONA STATE COLLEGE - MCKINNON HALL (2006:901) | 1200 W INTERNATIONAL SPEEDWAY BLVD
6049 | LANZA RESIDENCE | 1317 N ATLANTIC AVE
6050 | EXTRA SPACE STORAGE | 410 CONSTANT FRIENDSHIP BLVD.
6051 | FORUM CORPORATE PARKWAY BLDG | 9160 FORUM CORPORATE PARKWAY
6052 | ODYSSEY BUILDING (AUTISM) | 5215 W LAUREL STREET
6053 | MILLENIA LAKES BUILDING (2018:109 - LSI) | 5323 MILLENIA LAKES BLVD.
6054 | CREIGHTON/BAYOU BLDG. (2018:106 - AUTISM INSTITUTE) | 4900 BAYOU BLVD | 2989
6055 | MURFREESBORO PIKE BUILDING | 900 MURFREESBORO PIKE
6056 | MISSOURI AVE BLDG | 1225 MISSOURI AVE N | 100
6057 | HARDEN BLVD BLDG | 2190 HARDEN BLVD | 50
6058 | FT. PIERCE REGIONAL MEDICAL FACILITY | 2498 S 35TH ST
6060 | MADISON ST. BLDG | 805 W. MADISON ST
6061 | DIAZ RESIDENCE | 5452E MICHIGAN ST
6062 | DELEVOE RESIDENCE | 739 SW 4TH TERRACE
6063 | AMICK RESIDENCE | 54 EDGEWOOD DR
6064 | BETTER BUSINESS BUREAU OF PALM BEACH CO., INC (2019:103 - JMI) | 4411 BEACON CIRCLE
6065 | THE CLOCK BUILDING | 200 W. COLLEGE AVE. | 2011
6066 | COM - SARASOTA REGIONAL CAMPUS (2019:161) | 5590 BEE RIDGE RD
6067 | THE STORAGE CENTER 2 | 3110 APALACHEE PARKWAY | 150
6068 | COM - FLORIDA MEDICAL PRACTICE PLAN (2019:104) | 1126 LEE AVENUE | 613
6069 | MIAMI-DADE COURTHOUSE | 111 NW 1ST STREET
6070 | CENTER FOR PREVENTION AND EARLY INTERVENTION (CPEI) | 305 W CRAWFORD ST
6071 | 2020:108 | 156 MILESTONE WAY
6072 | JACKSON BLUFF HOUSE | 2013 JACKSON BLUFF RD
6073 | KAREN LANE HOUSE | 1229 KAREN LN
6074 | BUFFORD STREET HOUSE | 1821 BUFFORD ST
6075 | SAN PIPER HOUSE | 2221 SAN PIPER ST
6076 | RR SQ 607 MCDONNELL BUILDING | 607 MCDONNELL DR
6077 | FLORIDA VIRTUAL CAMPUS (2020:110 - NWRDC) | 1753 W PAUL DIRAC DR | 33505
6078 | KING STREET BLDG (2021:109 - CPEI) | 343 E KING ST | 3603
6079 | COCA (COUNCIL ON CULTURAL & ARTS) - (2021:113 - OPENING NIGHTS) | 816 S MLK JR BLVD
6080 | UNIVERSITY GREEN CONDOMINIUMS (2021:114 - TEMP. HOUSING) | 1972 ANN ARBOR AVE
6081 | 2004 CORVALLIS AVE | 2004 CORVALLIS AVE
6082 | 1988 ANN ARBOR AVE | 1988 ANN ARBOR AVE
6083 | 2009 CORVALLIS AVE | 2009 CORVALLIS AVE
6084 | COM - TALLAHASSEE REGIONAL CAMPUS (2021:112) | 2619 CENTENNIAL BLVD
6085 | OLD ST AUG BLDG (2022:101 - FCPR, FL CTR FOR PREVENTION RESEARCH) | 2200 OLD ST AUGUSTINE RD | 1500
6086 | FLORIDA STATE-SOUTHWOOD SHARED RESOURCE CENTER | 2585 SHUMARD OAK BLVD | 28974
6087 | COM - FLORIDA MEDICAL PRACTICE PLAN (2023:102) | 2507 CALLAWAY RD
6087 | ***INVALID*** COM - FLORIDA MEDICAL PRACTICE PLAN (2023:102) ***INVALID*** | 2507 CALLAWAY ROAD
6088 | THE COLLEGIATE SCHOOL (2023:003) | 2480 ST. ANDREWS BLVD
6502 | LEASE - 2013:102 - CITY PLACE | 477 S ROSEMARY AVE | 13595
6502 | LEASE - 2013:102 - CITY PLACE | 477 S ROSEMARY AVE
6599 | DIGITAL DOMAIN HOUSING | 215 ARLINGTON ROAD
6600 | MIAMI-DADE COURTHOUSE | 111 NW 1ST STREET
0670 | REID RESIDENCE | 320 SPRING RIDGE DR
0671 | WATKINS RESIDENCE | 428 CROSSWICK RD
0672 | CAWLEY RESIDENCE | 6 FERNS CT
7015 | REZ GARAGE 1 | 3226 FLASTACOWA WAY | 576
7016 | REZ RENEGADE PAVILION | 3226 FLASTACOWO RD | 200
7017 | REZ LARGE POLE SHED | 3226 FLASTACOWO RD | 1600
7018 | REZ GOLD PAVILION | 3226 FLASTACOWO RD | 100
7019 | REZ CHICKEE | 3226 FLASTACOWO RD | 50
7020 | REZ GARNET PAVILION | 3226 FLASTACOWO RD | 50
7021 | REZ COVERED SHED/PARKING | 3226 FLASTACOWO RD | 120
7022 | REZ HIGH ROPES PAVILION | 3226 FLASTACOWO RD | 1520
7023 | HIGH ROPES COURSE | 3226 FLASTACOWO RD | 600
8001 | IM FIELDS FIELDS CONTROL BLDG. | 3950 TYSON RD | 6321
8002 | IM FIELDS MAINTENANCE BLDG. | 3952 TYSON RD | 6950
8003 | IM FIELDS SOFTBALL CONTROL | 3954 TYSON RD | 4313
8004 | IM FIELDS REC SPORTSPLEX BLDG. | 3950 TYSON RD | 7012
8005 | I.M. FIELD CONTROL STORAGE BUILDING | 3950 TYSON RD | 189
8006 | I.M. FIELD MAINTENANCE STORAGE BUILDING | 3952 TYSON RD | 189
8008 | MORCOM AQUATICS CTR. | 2560 POTTSDAMER ST | 8372
8009 | MORCOM AQUATICS MECH. BLDG. | 2560 POTTSDAMER ST | 2457
8010 | MULTI-PURPOSE EDUCATION FACIL. | 2566 POTTSDAMER ST | 47238
8018 | WFSU-TV TRANSMITTER BLDG | 1600 RED BARBER PLAZA | 466
8020 | FSU POLICE DEPARTMENT STORAGE BUILDING | 169 HERLONG DR | 823
8050 | FHP ACADEMY | 2908 RIDGEWAY ST | 43564
8051 | FHP DORM | 2908 RIDGEWAY ST | 24159
8052 | COLLEGE OF MEDICINE - FSU PRIMARYHEALTH | 2911 ROBERTS AVE | 9986
8053 | PRIMARYHEALTH PORTE-COCHERE | 2911 ROBERTS AVE | 925
8060 | GOLF COURSE - STORAGE | 2000 WEST ORANGE AVE | 93
8061 | GOLF COURSE - FUEL STORAGE | 2000 WEST ORANGE AVE | 66
8062 | GOLF COURSE - FERTILIZER STORAGE | 2000 WEST ORANGE AVE | 66
8063 | GOLF COURSE - PUMP HOUSE | 2550 POTTSDAMER ST | 679
8064 | GOLF COURSE - PUMP HOUSE (DUPLICATED 8063) | 2550 POTTSDAMER ST | 600
8088 | NURSERY - BAT HOUSE | 1800 ORANGE AVE | 81
8089 | GROUNDS EQUIPMENT POLE BARN | 170 HERLONG DRIVE
9001 | RINGLING- ART MUSEUM | 5401 BAY SHORE RD | 114190
9002 | RINGLING- CA'D'ZAN | 5401 BAY SHORE RD | 27178
9003 | RINGLING- CIRCUS MUSEUM | 5401 BAY SHORE RD | 35292
9004 | RINGLING- GROUNDS BLDG. | 5401 BAY SHORE RD | 5871
9005 | RINGLING- CARETAKER'S HOUSE | 5401 BAY SHORE RD | 2804
9006 | RINGLING- NORTH GATEHOUSE | 5401 BAY SHORE RD | 814
9007 | RINGLING- PUMPHOUSE | 5401 BAY SHORE RD | 639
9008 | RINGLING - ASOLO THEATER | 5555 TAMIAMI TRAIL
9009 | RINGLING - GREENHOUSE | 5555 TAMIAMI TRAIL
9010 | RINGLING- WEST WING | 5401 BAY SHORE RD | 48089
9011 | RINGLING- BANYAN CAFE | 5401 BAY SHORE RD | 5298
9012 | RINGLING - OFFICE TRAILER #1 | 5555 TAMIAMI TRAIL | 840
9013 | RINGLING - MUSEUM ANNEX | 5555 TAMIAMI TRAIL
9014 | RINGLING- PUMPHOUSE #2 | 5401 BAY SHORE RD | 450
9015 | RINGLING - OFFICE TRAILER #2 | 5555 TAMIAMI TRAIL | 720
9016 | RINGLING - STORAGE TRAILER | 5555 TAMIAMI TRAIL | 432
9017 | RINGLING - TICKET BOOTH | 5555 TAMIAMI TRAIL | 100
9018 | RINGLING- UTILITIES PLANT | 5401 BAY SHORE RD | 6341
9019 | RINGLING- VISITOR'S PAVILION | 5401 BAY SHORE RD | 54188
9020 | RINGLING- TIBBALS LEARNING CTR | 5401 BAY SHORE RD | 60921
9021 | RINGLING- JOHNSON-BLALOCK CTR. | 5401 BAY SHORE RD | 70123
9022 | RINGLING- FACILITIES ADMIN. | 5401 BAY SHORE RD | 2454
9023 | RINGLING- PUMPHOUSE #3 | 5401 BAY SHORE RD | 56
9024 | RINGLING- BOLGER PLAYSPACE 3-LV | 5401 BAY SHORE RD | 300
9025 | RINGLING- BOLGER PLAYSPACE TP | 5401 BAY SHORE RD | 100
9026 | RINGLING- TEA HOUSE | 5401 BAY SHORE RD | 420
9027 | RINGLING TALLEVAST WAREHOUSE | 500 TALLEVAST ROAD
9027 | CONSTANT FRIENDSHIP BLVD. BLDG | 410 CONSTANT FRIENDSHIP BLVD.
9028 | RINGLING- WAREHOUSE | 3135 N WASHINGTON BLVD | 7141
9999 | NO BLDG DESIGNATED
ADMIN | FACILITIES OVERHEAD COSTS
BLUE LIGHT0001 | BLUE LIGHT - FACILITY - 0001 - ALLIGATOR POINT
BLUE LIGHT0004 | BLUE LIGHT - FACILITY 0004 - MAIN CAMPUS
BLUE LIGHT0005 | BLUE LIGHT - FACILITY 0005 - MISSION ROAD STATION
BLUE LIGHT0006 | BLUE LIGHT - FACILITY 0006 - PLANT STREET
BLUE LIGHT0007 | BLUE LIGHT - FACILITY 0007 - SEMINOLE RESERVATION
BLUE LIGHT0008 | BLUE LIGHT - FACILITY 0008 - SOUTHWEST CAMPUS
BLUE LIGHT0012 | BLUE LIGHT - FACILITY 0012 BELLEVUE
BLUE LIGHT0013 | BLUE LIGHT - FACILITY 0013 - S TECH INOVATION PARK
BLUE LIGHT0014 | BLUE LIGHT - 0014 - MEDICAL SCHOOL
BLUE LIGHT0016 | BLUE LIGHT - FACILITY 0016 - CLASSES IN/OUT
BLUE LIGHT0017 | BLUE LIGHT - FACILITY 0017 - ENGINEERING
BLUE LIGHT0018 | BLUE LIGHT - FACILITY 0018 - INNOVATION PARK
BLUE LIGHT0020 | BLUE LIGHT - FACILITY 0020 - SOUTHWOOD
BLUE LIGHT0021 | BLUE LIGHT - FACILITY 0021 - KLEMAN PLAZA
BLUE LIGHT0023 | BLUE LIGHT - FACIITY 0023 - HERITAGE GROVE
C001 | COMMUNICATIONS COMPOUND - M L TRACK | 101 PSYCHOLOGY WAY
C002 | COMMUNICATIONS COMPOUND - PALM COURT | 524 PALM COURT
ELECMANHOLES | ELECTRIC MANHOLES | CAMPUS WIDE
F001 | BOBBY BOWDEN FIELD | UNIVERSITY CENTER/CAMPBELL STADIUM | 0
F002 | DUNLAP PRACTICE FIELDS | UNIVERSITY CENTER/HOWSER STADIUM | 0
F003 | MIKE MARTIN FIELD | HOWSER STADIUM | 0
F004 | SAND VOLLEYBALL COURTS | SPIRIT WAY | 0
F005 | MARCHING CHIEFS PRACTICE FIELD | CHIEFTAN WAY | 0
F006 | FOOTBALL SOD CEMETERY | EAST OF DUNLAP FIELDS | 0
F008 | HAMMER THROW PRACTICE FIELD | LEVY AVENUE AND PENNELL CIRCLE | 0
F009 | PIT - CONCRETE SCRAPS | 2201 EISENHOWER STREET | 0
F010 | IM FIELDS - SOCCER | 3950 TYSON RD | 0
F011 | IM FIELDS - FOOTBALL | 3950 TYSON RD | 0
F012 | IM FIELDS - SOFTBALL | 3954 TYSON RD | 0
F013 | SEMINOLE SOCCER FIELD | SPIRIT WAY | 0
F014 | JOANNE GRAF SOFTBALL FIELD | SPIRIT WAY | 0
F015 | MIKE LONG TRACK & FIELD | CHIEFTAN WAY | 0
FIRE | FIRE SERVICE FEES | CAMPUS WIDE
FOUNTAINS | FOUNTAINS ON CAMPUS
G001 | WESTCOTT PLAZA | 222 S COPELAND ST | 51468
G002 | MINA JO POWELL ALUMNI GREEN | CONVOCATION WAY | 47525
G003 | LANDIS GREEN | BETWEEN COLLEGIATE LOOP AND HONORS WAY | 142767
G004 | GREEK PARK | UNIVERSITY WAY, GRAY ST., & W. JEFFERSON | 85172
G005 | WOODWARD STREET PLAZA | N WOODWARD AVE | 12393
G006 | UNION GREEN | SOUTH OF OGLESBY STUDENT UNION | 82513
G007 | VILLAGE GREEN | 300 M L KING BLVD S | 51427
G008 | LANGFORD GREEN | CHAMPIONS WAY | 68070
G009 | WALKER PLAZA | CHAMPIONS WAY | 16889
G010 | FLYING HIGH CIRCUS | CHIEFTAN WAY | 73757
G011 | OGLESBY UNION COURTYARD | N WOODWARD AVE | 0
G012 | SPORTSMANSHIP PLAZA | GATE G, CAMPBELL STADIUM | 0
G013 | UNIVERSITY CENTER GATES PLAZA | GATE K, CAMPBELL STADIUM | 0
G014 | OWEN SELLERS AMPHITHEATRE | KUERSTEINER MUSIC BUILDING | 0
G015 | EPPES GREEN | EPPES BLDG | 0
G016 | SPEICHER MEMORIAL PLAZA | 121 CHIEFTAN WAY
G017 | REZ LAKEFRONT PARK | 3226 FLASTACOWO RD | 0
G018 | DON VELLER SEMINOLE GOLF COURSE | 2550 POTTSDAMER ST
G019 | LABYRINTH | 1111 W CALL ST
G020 | CALL AND MURPHREE STORM WATER POND | CALL AND MURPHREE ST
G021 | LAKE ELBERTA FACILITY | LAKE BRADFORD RD
G022 | PEPPER DRIVE STORM WATER POND | PEPPER DRIVE
G023 | OCONNELL PROPERTY - WEST | 402 W GAINES ST
G024 | CITY BIKE TRAIL | OCALA TO STADIUM
G025 | CHATMAN'S PLACE | 142 COLLEGIATE LOOP
GROUNDS | CAMPUS AREAS
HERITAGE GROVE | HERITAGE GROVE | 1947 HERITAGE GROVE CIR
HYDRANT | FIRE HYDRANTS
HYDRANTS | FIRE HYDRANTS
INNOVATION PARK | INNOVATION PARK
IRRIGATION0001 | IRRIGATION SYSTEMS
IRRIGATION0004 | IRRIGATION SYSTEMS
IRRIGATION0005 | IRRIGATION SYSTEMS
IRRIGATION0006 | IRRIGATION SYSTEMS
IRRIGATION0007 | IRRIGATION SYSTEMS
IRRIGATION0008 | IRRIGATION SYSTEMS
IRRIGATION0012 | IRRIGATION SYSTEMS
IRRIGATION0013 | IRRIGATION SYSTEMS
IRRIGATION0014 | IRRIGATION SYSTEMS
IRRIGATION0016 | IRRIGATION SYSTEMS
IRRIGATION0017 | IRRIGATION SYSTEMS
IRRIGATION0018 | IRRIGATION SYSTEMS
IRRIGATION0020 | IRRIGATION SYSTEMS
IRRIGATION0021 | IRRIGATION SYSTEMS
IRRIGATION0023 | IRRIGATION SYSTEMS
L0201 | MAG LAB STORAGE BUILDING
L021 | 2010:115-NHMFL STORAGE | 1531 COMMONWEALTH BUSINESS DR | 2400
L023 | FCRR PENSACOLA | 5625 DIXIE DRIVE
L025 | LEASE - ROBDOL, LLC | 385C E JEFFERSON ST
L037 | LEASE - 2013:109 - FLORIDA INCLUSION NETWORK | 3758 MARYWEATHER LN
MAIN CAMPUS | MAIN CAMPUS
NW CAMPUS | NW CAMPUS
OUTDR LGHT-0001 | OUTDOOR LIGHTING - FACILITY 0001 - ALLIGATOR POINT
OUTDR LGHT-0004 | OUTDOOR LIGHTING - FACILITY 004 - MAIN CAMPUS | OUTDOOR LIGHTS ON CAMPUS
OUTDR LGHT-0005 | OUTDOOR LIGHTING - FACILITY 0005 - MISSION ROAD STATION
OUTDR LGHT-0006 | OUTDOOR LIGHTING - FACILITY 0006 - PLANT STREET
OUTDR LGHT-0007 | OUTDOOR LIGHTING - FACILITY 0007 - RESERVATION
OUTDR LGHT-0008 | OUTDOOR LIGHTING - FACILITY 0008 - SOUTHWEST CAMPUS
OUTDR LGHT-0012 | OUTDOOR LIGHTING - FACILITY 0012 - LEASES
OUTDR LGHT-0013 | OUTDOOR LIGHTING - FACILITY 0013 - S TECH INNOVATION PARK
OUTDR LGHT-0014 | OUTDOOR LIGHTING - FACILITY 0014 - MEDICAL SCHOOL
OUTDR LGHT-0016 | OUTDOOR LIGHTING - FACILITY 0016 - CLASSES IN/OUT
OUTDR LGHT-0017 | OUTDOOR LIGHTING - FACILITY 0017 - ENGINEERING
OUTDR LGHT-0018 | OUTDOOR LIGHTING - FACILITY 0018 - INNOVATION PARK
OUTDR LGHT-0020 | OUTDOOR LIGHTING - FACILITY 20 - SOUTHWOOD
OUTDR LGHT-0021 | OUTDOOR LIGHTING - FACILITY 0021 - KLEMAN PLAZA
OUTDR LGHT-0023 | OUTDOOR LIGHTING - FACILITY 0023 - HERITAGE GROVE
P128 | PENSACOLA-COPELAND - LOT 128 | 608 W PENSACOLA ST
P138 | SOUTH SIDE OF PENSACOLA AND EAST OF GRAY | 657 W PENSACOLA ST
P140 | THE LAB PARKING | 601 W LAFAYETTE ST
P183 | PARKING LOT ADJACENT TO AOPI (ALPHA OMICRON PI) HOUSE | 657 W PENSACOLA ST | 8027
P209 | PARKING LOT NE OF UKIRK | 541 PALM CT
P210 | PARKING LOT AT BLDG 0438 | 525 W CALL ST
P212 | CALL & MACOMB LOT | 515 W CALL ST | 0
P214 | PALM CT TO W CALL | 539 PALM COURT | 0
P233 | CONRADI LOT | 710 W CALL ST | 0
P347 | UNPAVED LOT WEST OF GARAGE #6 | 413 VARSITY DR
P365 | HENDRY ST. LOT | 1532 HENDRY ST.
PARKING LOTS | PARKING LOTS ON CAMPUS
RESERVATION | RESERVATION
RS01 | WFSU-TV REPEATER STATION #1 | 301 NW AVENUE E
RS02 | WFSU-TV REPEATER STATION #2 | STATE ROAD 73
RS03 | TALLAHASSEE ELECTRIC SUB STATION | MACLAY COMMERCE DRIVE | 900
SOUTHWOOD | SOUTHWOOD
STEAMMANHOLES | STEAM MANHOLES
SW CAMPUS | SW CAMPUS
T500 | T500 BUILDING | 0500 TEST
TEMP_LEASE | PROCEDURAL USE ONLY
U001 | WELL PUMPS FOR STADIUM CHILLERS | BETWEEN CIRCUS / BAND FIELD
U1060 | 1060 W PENSACOLA ST ML | 1060 W PENSACOLA ST ML
U1213 | 288 CHAMPIONS WAY | 1213 W PENSACOLA STREET
U1213A | 288 CHAMPIONS WAY | 1213 W PENSACOLA ST E&G
U1213B | 288 CHAMPIONS WAY | 1213 W PENSACOLA ST CLUB
U1215RF | 1215 W PENSACOLA ST UNIVERSITY CTR | 1215 W PENSACOLA STREET
U1239 | IRRIGATION TIMER CLOCK | 1239 W STADIUM DR
U1240 | TRAFFIC LIGHT | 1240 W PENSACOLA ST
U1301 | IRRIGATION METER | 1301 PENSACOLA ST
U1315 | 1315 E LAFAYETTE ST STE C | 1315 E LAFAYETTE ST C
U1339A | 1339 E LAFAYETTE ST A | 1339 E LAFAYETTE ST A
U1339B | 1339 E LAFAYETTE ST B | 1339 E LAFAYETTE ST B
U1339C | 1339 E LAFAYETTE ST C | 1339 E LAFAYETTE ST C
U1339D | 1339 E LAFAYETTE ST D | 1339 E LAFAYETTE ST D
U1339E | 1339 E LAFAYETTE ST E | 1339 E LAFAYETTE ST E
U1339F | 1339 E LAFAYETTE ST F | 1339 E LAFAYETTE ST F
U1505 | 1505 W THARPE ST APT 1524 | 1505 W THARPE ST APT 1524
U904 | SALLEY HALL TENNIS COURTS | HULL DR.
U9157 | 157 HERLONG DR 9 & 10 | 157 HERLONG DR 9 & 10
U9200 | IRRIGATION METER | 200 CHAMPIONS WAY
U9218 | 218 S WILDWOOD DR CONTRACTOR | 218 S WILDWOOD DR CONTRAC
U9303 | CONSTRUCTION TRAILER UTILITIES | 303 W STADIUM DR
U9317 | 317 N COPELAND STREET | 317 N COPELAND STREET
U9319 | 319 HENDRY ST | 319 HENDRY ST
U9397 | CNG 397 W STADIUM DR | 397 W STADIUM DR
U9400 | CNG 400 CHAMPIONS WAY | 400 CHAMPIONS WAY
U9403 | 403 CHIEFTAN WAY IRRIGATION | 403 CHIEFTAN WAY IRRIGATI
U9410 | IRRIGATION METER | 410 CHEIFTAIN WAY
U9427 | 427 DUNWOODY STREET | 427 DUNWOODY STREET
U9430 | 430 S WOODWARD AVENUE | 430 S WOODWARD AVENUE
U9514 | 514 MURPHREE STREET | 514 MURPHREE STREET
U9517 | UTIL - BLUE LIGHT METER | 517 MURPHREE ST
U9552 | 552 W COLLEGE AVE | 552 W COLLEGE AVE
U9600 | 600 W PENSACOLA ST | 600 W PENSACOLA ST
U9606 | 606 W PENSACOLA ST | 606 W PENSACOLA ST
U9644 | 644 MCDONNELL DRIVE | 644 MCDONNELL DRIVE
U9650 | 650 W JEFFERSON ST | 650 W JEFFERSON ST
U9808 | 808 W TENNESSEE ST DORM | 808 W TENNESSEE ST DORM
U9808T | 808 W TENNESSEE ST TUNNEL | 808 W TENNESSEE ST TUNNEL
U9810 | 810 W TENNESSEE ST | 810 W TENNESSEE ST
U9820 | 820 W MADISON ST | 820 W MADISON ST
U9929 | PARKING GARAGE FULL SIGN | 929 W TENNESSEE ST
U9998 | DAIRY BARN | DAIRY BARN
U9999 | TRAFFIC LIGHT | WOODWARD & CROSSWALK
UCTR | UNIVERSITY CENTER INTERNAL REFUSE E&G | UNIVERSITY CENTER E&G
UTILITIES | UTILITIES INFRASTRUCTURE | MAIN CAMPUS UTILITIES
UTILITY FEES | UTILITY FEES | CAMPUS WIDE
UTL-CONST | UTILITY CONSTRUCTION METERS | CAMPUS
V147 | VACANT LOT 147 | 700 W. ST. AUGUSTINE
V503 | VACANT LOT - ST. AUG AND S. WOODWARD | 503 S WOODWARD AVE
V818 | VACANT LOT 818 | 818 W. ST. AUGUSTINE
VEHICLES0004 | VEHICLE COST TRACKING
VEHICLES0018 | 0018 VEHICLE COST TRACKING
W001 | BLDG 89 TO WEST - WALKWAY | 114 N COPELAND ST | 1289
W002 | BLDG 89 TO 54 - WALKWAY | 122 N COPELAND ST | 2620
W003 | VILLAGE GREEN COLONNADE | 308 S M L KING JR BLVD | 2118
W004 | BLDG. 40 TO 36 - WALKWAY | 117 N WOODWARD AVE | 1950
W005 | BLDG. 41 TO 45 TO 42 - WALKWAY | 1055 ATOMIC WAY | 7440
W006 | BLDG. 39 TO 146 TO 38 -WALKWAY | 89 CHIEFTAN WAY | 2120
W008 | COM - WALKWAYS | COLLEGE & COPELAND
W009 | TENNESSEE STREET PEDESTRIAN TUNNEL | 810 W TENNESSEE ST | 750
W010 | PENSACOLA ST PEDESTRIAN TUNNEL | INTERSECTION OF PENSACOLA AND STADIUM | 1000
W011 | WOODWARD TUNNEL | 900 ACADEMIC WAY | 501
W050 | P.C.- WALKWAY (1005 TO 1007) | 4750 COLLEGIATE DR. | 3500
W051 | P.C.- WALKWAY (1007 TO 1006) | 4750 COLLEGIATE DR. | 1896
W055 | MARINE LAB- COVERED WALKWAY | 3618 COASTAL HIGHWAY 98 | 50
ZONE1 | MULTIPLE BUILDINGS IN ZONE 1
ZONE2 | MULTIPLE BUILDINGS IN ZONE 2
ZONE3 | MULTIPLE BUILDINGS IN ZONE 3
ZONE4 | MULTIPLE BUILDINGS IN ZONE 4
ZONE5 | MULTIPLE BUILDINGS IN ZONE 5 | 1721 W PAUL DIRAC DR
ZONE6 | MULTIPLE BUILDINGS IN ZONE 6
ZONEA | MULTIPLE BUILDINGS IN ZONE A
ZONEB | MULTIPLE BUILDINGS IN ZONE B
ZONEC | MULTIPLE BUILDINGS IN ZONE C
ZONED | MULTIPLE BUILDINGS IN ZONE D